| MEEKAS STAR ENGINEERING | EC&I METHOD STATEMENT REGISTER |
| --- | --- |
| PROJECTS DEPARTMENT · EC&I CONSTRUCTION · METHOD STATEMENT REGISTER | MSE-HSE-MS-001 · Rev 01 · 2025 |

EC&I CONSTRUCTION

METHOD STATEMENT REGISTER

OHS ACT 85/1993  ·  CONSTRUCTION REGULATIONS 2014  ·  SANS 10142  ·  IEC 60364  ·  IEC 60079

| Document Number | MSE-HSE-MS-001 · Rev 01 · 2025 |
| --- | --- |
| Principal Contractor | Meekas Star Engineering Service Limited — Projects Department |
| Project Name | [Insert Project Name] |
| Project Number | [Insert Project Number] |
| Client / EPCM | [Insert Client Name] |
| Site Location | [Insert Site Location] |
| Scope | EC&I Construction — Full scope from OHL through to instrument loop testing & energisation |
| Prepared By | [Name] — [Role] |
| Approved By | [Name] — Manager, Projects |
| Client Acceptance | [Name] — [Role] — [Date] |
| Related Documents | MSE-HSE-RA-001 (Risk Assessment Register) ¦ MSE-HSE-SF-001 (Safety File) |
| Review Frequency | Before each new activity phase or after any incident affecting the scope of work |

⚠  THESE METHOD STATEMENTS MUST BE BRIEFED TO ALL WORKERS BEFORE WORK COMMENCES. WORKERS MUST SIGN THE ACKNOWLEDGEMENT TABLE IN EACH METHOD STATEMENT. NO WORK MAY PROCEED WITHOUT THIS BRIEFING.

| Prepared By | Reviewed By | Approved By | Client Approval |
| --- | --- | --- | --- |
| [Name] — [Role] | EC&I Site Manager | [Name] — Manager Projects | [Name] — [Company] |
| Signature: _______________________ | Signature: _______________________ | Signature: _______________________ | Signature: _______________________ |
| Date: ___________________________ | Date: ___________________________ | Date: ___________________________ | Date: ___________________________ |

| MEEKAS STAR ENGINEERING | TABLE OF CONTENTS |
| --- | --- |
| PROJECTS DEPARTMENT · EC&I CONSTRUCTION · METHOD STATEMENT REGISTER | MSE-HSE-MS-001 |

| MS Ref | RA Ref | Method Statement Title | Document Ref | Page |
| --- | --- | --- | --- | --- |
| MS-001 | RA-001 | Cable Ladder & Tray Installation | MSE-HSE-MS-001-01 | — |
| MS-002 | RA-002 | Cable Pulling Operations | MSE-HSE-MS-001-02 | — |
| MS-003 | RA-003 | Isolation, Lockout & Tagout (LOTO) | MSE-HSE-MS-001-03 | — |
| MS-004 | RA-005 | 33kV OHL — Stringing, Hardware & Terminations | MSE-HSE-MS-001-04 | — |
| MS-005 | RA-008 | Earthing Mat & Grid Installation | MSE-HSE-MS-001-05 | — |
| MS-006 | RA-010 | Pre-Commissioning, Loop Testing & System Energisation | MSE-HSE-MS-001-06 | — |

MS-001 — Cable Ladder & Tray Installation MSE-HSE-MS-001-01

| MS Reference | MS-001 |
| --- | --- |
| Related RA | RA-001 (MSE-HSE-RA-001 — Risk Assessment Register) |
| Document Number | MSE-HSE-MS-001-01 |
| Project | [Project Name] |
| Prepared By | [Name] — [Role] |
| Approved By | [Name] — Manager, Projects |
| Date Prepared | [DD/MM/YYYY] |
| Review Date | [DD/MM/YYYY or after any scope change or incident] |
| Supervisor in Charge | [Name] |
| Gang / Discipline | [EC&I / OHL / Instrument / etc.] |

1. SCOPE & PURPOSE

This Method Statement describes the safe step-by-step procedure for the installation of cable ladder, cable tray, and associated supports — including setting out, support installation, working at height, and earthing of cable ladder systems.

2. PRE-CONDITIONS — DO NOT START WITHOUT CONFIRMING ALL ITEMS BELOW

⚠  STOP: Every item in this section must be confirmed BEFORE work commences. If ANY item cannot be confirmed — work does NOT start. Notify EC&I Site Manager.

- ☐  AFC drawing issued and available on site

- ☐  Materials received, inspected, and stored correctly

- ☐  MRIR for ladder/tray materials signed by QC Officer

- ☐  PTW issued if work is within 1m of any energised equipment

- ☐  Scaffold inspected and tagged GREEN, or MEWP inspected and certified

- ☐  Toolbox talk completed — this method statement briefed to all workers

- ☐  PPE inspected and issued to all workers

3. PERSONAL PROTECTIVE EQUIPMENT (PPE)

| PPE Item | Standard / Specification | Mandatory? |
| --- | --- | --- |
| Safety helmet (hard hat) | SANS 1397 | MANDATORY |
| Safety boots — steel toe & steel midsole | SANS 20345 | MANDATORY |
| High-visibility vest | EN 471 Class 2 | MANDATORY |
| Safety glasses | SANS 1425 | MANDATORY |
| Work gloves — leather or cut-resistant | EN 388 | MANDATORY |
| Full body harness + double lanyard | SANS 1354 | MANDATORY — above 2m |
| Face shield | ANSI Z87.1 | When overhead drilling or cutting |
| P2 dust mask / respirator | SANS 1412 | When drilling concrete |
| Hearing protection (ear plugs or muffs) | 85dB+ areas | When using power tools |

4. TOOLS, EQUIPMENT & MATERIALS

| # | Tool / Equipment / Material | Specification / Standard | Qty Required | Inspected? |
| --- | --- | --- | --- | --- |
| 1 | Cable ladder sections (as per BOM) | Per engineering drawing | As per IFC | ☐ |
| 2 | Cable ladder supports / cleats / hangers | Per engineering spec | As per BOM | ☐ |
| 3 | Stainless steel or hot-dip galv fixings | Per corrosion specification | As per BOM | ☐ |
| 4 | M10/M12 anchor bolts — tested and rated | Manufacturer rated | As required | ☐ |
| 5 | Hacksaw / angle grinder with metal disc | Max 230mm disc, guarded | As required | ☐ |
| 6 | Hand drill / rotary hammer drill | Correct bit for substrate | 1 per gang | ☐ |
| 7 | Spirit level + laser level | Calibrated | 1 per gang | ☐ |
| 8 | Torque wrench | Calibrated — to correct Nm spec | 1 per gang | ☐ |
| 9 | Earthing conductor + clamps | Per SANS 10142 | As per drawing | ☐ |
| 10 | Earth continuity test instrument | Calibrated | 1 | ☐ |
| 11 | Full body harness, double lanyard | SANS 1354, pre-use inspection | 1 per elevated worker | ☐ |
| 12 | Cable drum trolley / mechanical handling aid | Rated for load | As required | ☐ |

5. STEP-BY-STEP SAFE WORK PROCEDURE

STEP 1.  PRE-WORK CHECKS

- Verify AFC drawing is the correct revision. Do NOT work from superseded drawings.

- Walk the cable ladder route. Identify all potential conflicts — pipe, HVAC, existing equipment, low headroom, ATEX zones.

- Confirm the substrate (concrete, steelwork, GRP) to determine correct anchor type and drill bit.

- Confirm services location — do NOT drill without a CAT scan result or confirmed services drawing clearance.

- Check scaffold is tagged GREEN and inspection date is within 7 days, OR MEWP is inspected with valid certificate.

- Confirm all workers have attended the TBT for today's activity, are wearing correct PPE, and have valid medical fitness certificates.

- PTW signed and in hand if working within 1m of any energised equipment or in any designated electrical area.

STEP 2.  MATERIAL STAGING & HANDLING

- Position cable drum trolley or materials handling trolley at work area access point.

- Cable ladder sections — carry maximum 2 persons per section. Never carry overhead without mechanical means.

- Stage materials within arm's reach of the work area. Do NOT overload scaffold platforms.

- Confirm all ladder sections are correct part number, length, material, and rung spacing per BOM.

STEP 3.  SETTING OUT SUPPORTS

- Mark support positions on structure per drawing — maximum span 1.5m unless otherwise specified on drawing.

- Use laser level to ensure support positions are level across the run. Check for gradient requirements on drawing.

- Mark all drilling positions with pencil or marker. Confirm no services within 50mm of proposed drill position (CAT scan mandatory).

STEP 4.  DRILLING & ANCHOR INSTALLATION

- Select correct drill bit for substrate — carbide for concrete, HSS for steelwork.

- Wear P2 dust mask and safety glasses (face shield for overhead drilling).

- Drill to correct depth per anchor specification. Clean hole with compressed air blast or vacuum.

- Install anchor bolt per manufacturer specification — check torque against specification using calibrated torque wrench.

- Do NOT exceed torque specification. Over-torquing will split concrete and compromise anchor strength.

- Record anchor installation in inspection register.

STEP 5.  CABLE LADDER / TRAY INSTALLATION

- Position ladder section onto supports — minimum 2 workers per section for sections >3m.

- Do NOT rest sections on anchor bolts before securing — support manually until bolt is engaged.

- Torque all couplers and joiners to specification — record in inspection log.

- At all changes of direction, use correct bend or tee section per drawing — do NOT force ladder around bends.

- Maintain minimum bend radius for cables that will be installed in this section — minimum 6× cable OD.

- Install all required separators for HV/LV/Instrument segregation as shown on drawing.

STEP 6.  WORKING AT HEIGHT

- Attach harness to certified anchor point BEFORE stepping onto elevated work platform.

- Never unclip from anchor until you have secured the second lanyard to a new anchor point — 100% tie-off at all times.

- No more than the rated number of workers on scaffold bay — never overload.

- All tools must be in a tool bag or tethered. No loose items on elevated work platforms.

- Exclusion zone below elevated work — barriers and signage in place before elevated work begins.

STEP 7.  EARTHING & BONDING

- Install earth continuity bonds at each coupling joint using green/yellow earth conductor and correct clamps.

- Bond to building main earth bar or designated earth point as shown on drawing.

- Test earth continuity with calibrated meter — resistance must be ≤ 1Ω per SANS 10142.

- Record results on IR Test Register (MSE-IR2-001). QC Officer to sign off.

STEP 8.  INSPECTION & HANDOVER

- Conduct final visual inspection — all fixings tight, all earth bonds in place, no sharp edges.

- De-burr all cut ends of ladder/tray. No exposed sharp edges that could damage cable sheaths.

- Complete Inspection Register (MSE-IR-001) for the completed ladder run.

- QC Officer to inspect and sign off. Photograph completed run — label photo with cable ladder ID.

- Housekeeping — clear all off-cuts, packaging, and waste from the area before end of shift.

6. INSPECTION HOLD POINTS & WITNESS POINTS

- QC Hold Point — anchor bolt torque inspection (QC Officer sign-off required before loading)

- QC Hold Point — earth continuity test ≤1Ω (QC Officer sign-off required)

- Witness Point — final inspection before cabling

7. EMERGENCY RESPONSE

EMERGENCY PROCEDURE — SPECIFIC TO THIS ACTIVITY:

In the event of a fall from height: Do NOT move the fallen person. Call for first aider immediately. Dial site emergency number. Notify site manager and Section 16(2). Preserve scene for investigation.

GENERAL: Site emergency number — [Insert]. National emergency: 10177. EC&I Site Manager: [Cell]. Section 16(2) [Name]: [Cell].

Muster point: [Insert location]. In any emergency — evacuate first, account for all persons, then report.

8. WORKER ACKNOWLEDGEMENT

I confirm that this Method Statement has been explained to me in a language I understand, that I understand the identified hazards and the controls to be applied, and that I will work in accordance with this procedure at all times.

| # | Full Name | ID Number | Trade / Role | Signature | Date |
| --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |
| 2 |  |  |  |  |  |
| 3 |  |  |  |  |  |
| 4 |  |  |  |  |  |
| 5 |  |  |  |  |  |
| 6 |  |  |  |  |  |
| 7 |  |  |  |  |  |
| 8 |  |  |  |  |  |
| 9 |  |  |  |  |  |
| 10 |  |  |  |  |  |
| 11 |  |  |  |  |  |
| 12 |  |  |  |  |  |

| Method Statement Author | Construction Supervisor | EC&I Site Manager | Section 16(2) Approved |
| --- | --- | --- | --- |
| [Name] | [Name] | [Name] | [Name] |
| Signature: _______________________ | Signature: _______________________ | Signature: _______________________ | Signature: _______________________ |
| Date: ___________________________ | Date: ___________________________ | Date: ___________________________ | Date: ___________________________ |

MS-002 — Cable Pulling Operations MSE-HSE-MS-001-02

| MS Reference | MS-002 |
| --- | --- |
| Related RA | RA-002 (MSE-HSE-RA-001 — Risk Assessment Register) |
| Document Number | MSE-HSE-MS-001-02 |
| Project | [Project Name] |
| Prepared By | [Name] — [Role] |
| Approved By | [Name] — Manager, Projects |
| Date Prepared | [DD/MM/YYYY] |
| Review Date | [DD/MM/YYYY or after any scope change or incident] |
| Supervisor in Charge | [Name] |
| Gang / Discipline | [EC&I / OHL / Instrument / etc.] |

1. SCOPE & PURPOSE

This Method Statement describes the safe step-by-step procedure for the installation (pulling) of all types and sizes of cable — including mechanical drum pulling, manual gang pulls, and single-cable draws through conduit, ladder, tray, and underground ducting.

2. PRE-CONDITIONS — DO NOT START WITHOUT CONFIRMING ALL ITEMS BELOW

⚠  STOP: Every item in this section must be confirmed BEFORE work commences. If ANY item cannot be confirmed — work does NOT start. Notify EC&I Site Manager.

- ☐  AFC cable schedule and routing drawing available

- ☐  Cable drum test certificate and drum sheet on site

- ☐  Ladder / tray installation inspected and signed off — no sharp edges

- ☐  PTW issued for any pull near energised equipment

- ☐  Mechanical cable pulling equipment inspected and tested — e-stop functional

- ☐  Cable drum spindle stand rated for drum weight — confirmed by inspection

- ☐  Toolbox talk completed — this method statement briefed to all workers

3. PERSONAL PROTECTIVE EQUIPMENT (PPE)

| PPE Item | Standard / Specification | Mandatory? |
| --- | --- | --- |
| Safety helmet | SANS 1397 | MANDATORY |
| Safety boots — steel toe | SANS 20345 | MANDATORY |
| High-visibility vest | EN 471 Class 2 | MANDATORY |
| Safety glasses | SANS 1425 | MANDATORY |
| Heavy-duty leather gloves | EN 388 Cut Level D+ | MANDATORY during pulling |
| Face shield | ANSI Z87.1 | During mechanical pulling — puller operator |
| Hearing protection | 85dB+ areas | When using mechanical puller |

4. TOOLS, EQUIPMENT & MATERIALS

| # | Tool / Equipment / Material | Specification / Standard | Qty Required | Inspected? |
| --- | --- | --- | --- | --- |
| 1 | Cable drum (correct drum per cable schedule) | Tested and tagged | Per schedule | ☐ |
| 2 | Cable drum spindle stand — rated for drum weight | Manufacturer rated SWL | 1 per drum | ☐ |
| 3 | Mechanical cable puller / winch | Rated for cable weight — with calibrated tension indicator | 1 | ☐ |
| 4 | Cable pulling grips (Kellems grips) | Rated for cable size | As required | ☐ |
| 5 | Swivels | Rated — matched to pulling load | As required | ☐ |
| 6 | Pulling eyes (terminating type) | Correct for conductor size | As required | ☐ |
| 7 | Cable lubricant (pulling compound) | Compatible with cable sheath material | As required | ☐ |
| 8 | Bell-mouth conduit entries | Correct ID for cable | All conduit entries | ☐ |
| 9 | Cable tags — brass or stainless | Per cable numbering schedule | 2 per cable | ☐ |
| 10 | Multimeter / continuity tester | Calibrated | 1 | ☐ |
| 11 | Measuring tape / cable counter | Calibrated | 1 | ☐ |

5. STEP-BY-STEP SAFE WORK PROCEDURE

STEP 1.  PRE-PULL PREPARATION

- Identify cable on schedule. Confirm drum number, cable type, voltage rating, size, and length.

- Verify cable is correct drum — check drum label against cable schedule. Do NOT mix drums.

- Position cable drum at pull start point — drum must unroll from top, not bottom, to prevent kinking.

- Chock drum on both sides immediately. Never release drum from transport without chocking.

- Install bell-mouth conduit entries at all conduit entry points to prevent cable sheath damage.

- Pre-lay cable lubricant (pulling compound) in conduit as per manufacturer instructions.

- Position mechanical puller at the pull end. Inspect: motor, brake, tension indicator, e-stop. Test e-stop before starting.

- Brief all gang workers on communication signals: PULL / STOP / EMERGENCY STOP. No ambiguity in signals.

STEP 2.  MECHANICAL PULLING SETUP

- Feed pulling rope through route — use draw-wire or fish tape. Never pull a rope with excessive force.

- Attach pulling grip (Kellems) correctly to cable end — correct grip for cable type. Never pull by the conductor alone.

- Connect pulling grip to swivel — swivel connected to pulling rope. No direct connection — swivel prevents torque transfer.

- Attach rated pulling eye to rope at puller end. Do NOT exceed cable's maximum pulling tension — calculate before pull.

- Maximum pulling tension: T = 1500 × conductor cross-section (mm²) × number of conductors. Never exceed. Reduce by 25% for bends.

- Ensure all workers are clear of the pull axis — no person between drum and puller at any time.

- Mechanical puller operator position: to the side — never behind the drum or in line with the cable.

STEP 3.  MANUAL GANG PULL

- For shorter pulls — gang pull under supervisor direction with clear communication.

- Gang leader at front, section feeders at each mid-point guide, drum supervisor at back.

- Pull on command 'PULL' — stop immediately on 'STOP'. Emergency shout = stop everything.

- Rotate gang positions every 15 minutes — same workers doing the same task continuously causes injury.

- Maximum gang pull per person: 25kg pulling force. For heavier cables — use mechanical pulling equipment.

STEP 4.  CABLE INSTALLATION

- Maintain even pulling speed — jerking causes conductor damage and grip failure.

- At every bend or change of direction — have a worker guiding the cable around the bend — do NOT allow cable to bind on ladder rungs.

- Monitor cable for kinking continuously — stop if kinking is observed. Straighten before proceeding.

- If cable stops moving — STOP. Do NOT increase force. Investigate cause. Re-lubricate if required.

- Do NOT exceed maximum pulling tension. If calculated tension is being approached — STOP. Re-assess route.

STEP 5.  CABLE IDENTIFICATION & TAGGING

- Immediately after pulling — tag both ends of the cable with correct cable number from cable schedule.

- Tags must be permanent, weatherproof, and match the cable schedule exactly.

- Record pulled cable on the Drawing Register (MSE-DWG-001) — ticking off each cable as it is installed.

- Measure and record actual installed length against drum label. Note any variance.

STEP 6.  POST-PULL CHECKS

- Visual inspection of cable along full route — no visible damage, sheath intact, no kinking.

- Insulation resistance test on completed cable runs — per MSE-IR2-001. Record pre-termination IR.

- Secure cable along ladder with ties at maximum 500mm intervals (instrumentation/LV), 750mm intervals (MV).

- Clear pull area — collect all rope, grips, swivels, drum packaging. Drum to be removed from area.

- Chock or remove cable drum spindle stands — no drums to be left unchocked on site.

6. INSPECTION HOLD POINTS & WITNESS POINTS

- Witness Point — drum identification check before pull (QC)

- QC Hold Point — IR test pre-termination (QC Officer sign-off)

- QC Hold Point — cable tagging verification (QC Officer)

7. EMERGENCY RESPONSE

EMERGENCY PROCEDURE — SPECIFIC TO THIS ACTIVITY:

Cable snap or grip failure: all workers clear of pull axis by procedure. In event of worker injury — stop all activities, call first aider, notify site manager, do not restart pull until incident investigated.

GENERAL: Site emergency number — [Insert]. National emergency: 10177. EC&I Site Manager: [Cell]. Section 16(2) [Name]: [Cell].

Muster point: [Insert location]. In any emergency — evacuate first, account for all persons, then report.

8. WORKER ACKNOWLEDGEMENT

I confirm that this Method Statement has been explained to me in a language I understand, that I understand the identified hazards and the controls to be applied, and that I will work in accordance with this procedure at all times.

| # | Full Name | ID Number | Trade / Role | Signature | Date |
| --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |
| 2 |  |  |  |  |  |
| 3 |  |  |  |  |  |
| 4 |  |  |  |  |  |
| 5 |  |  |  |  |  |
| 6 |  |  |  |  |  |
| 7 |  |  |  |  |  |
| 8 |  |  |  |  |  |
| 9 |  |  |  |  |  |
| 10 |  |  |  |  |  |
| 11 |  |  |  |  |  |
| 12 |  |  |  |  |  |

| Method Statement Author | Construction Supervisor | EC&I Site Manager | Section 16(2) Approved |
| --- | --- | --- | --- |
| [Name] | [Name] | [Name] | [Name] |
| Signature: _______________________ | Signature: _______________________ | Signature: _______________________ | Signature: _______________________ |
| Date: ___________________________ | Date: ___________________________ | Date: ___________________________ | Date: ___________________________ |

MS-003 — Isolation, Lockout & Tagout (LOTO) MSE-HSE-MS-001-03

| MS Reference | MS-003 |
| --- | --- |
| Related RA | RA-003 (MSE-HSE-RA-001 — Risk Assessment Register) |
| Document Number | MSE-HSE-MS-001-03 |
| Project | [Project Name] |
| Prepared By | [Name] — [Role] |
| Approved By | [Name] — Manager, Projects |
| Date Prepared | [DD/MM/YYYY] |
| Review Date | [DD/MM/YYYY or after any scope change or incident] |
| Supervisor in Charge | [Name] |
| Gang / Discipline | [EC&I / OHL / Instrument / etc.] |

1. SCOPE & PURPOSE

This Method Statement defines the mandatory procedure for the isolation and lockout/tagout of all energy sources before any person commences work on electrical equipment or systems. This procedure applies to ALL electrical isolation activities — from LV socket circuits to MV switchgear. NO EXCEPTIONS.

2. PRE-CONDITIONS — DO NOT START WITHOUT CONFIRMING ALL ITEMS BELOW

⚠  STOP: Every item in this section must be confirmed BEFORE work commences. If ANY item cannot be confirmed — work does NOT start. Notify EC&I Site Manager.

- ☐  LOTO equipment kit available — padlocks (one per worker), hasp, danger tags, lockout boxes

- ☐  PTW issued and signed by the authorised PTW issuer

- ☐  Approved voltage detection equipment (two units) calibrated and available

- ☐  Switching schedule prepared and independently verified for MV systems

- ☐  All workers who will be working on the isolated equipment have their own padlock

3. PERSONAL PROTECTIVE EQUIPMENT (PPE)

| PPE Item | Standard / Specification | Mandatory? |
| --- | --- | --- |
| Safety helmet | SANS 1397 | MANDATORY |
| Safety boots | SANS 20345 | MANDATORY |
| Safety glasses | SANS 1425 | MANDATORY |
| Electrically insulated gloves — LV rated (Class 00 min) | IEC 60903 Class 00+ | MANDATORY for all electrical work |
| Arc flash face shield (min 4 cal/cm² LV, 8–12 cal/cm² MV) | NFPA 70E / IEC 61482 | MANDATORY for panel access |
| Arc flash rated clothing (arc rated FR clothing) | ATPV rated to applicable cal/cm² | MANDATORY MV work |
| Rubber insulating mat | IEC 61111 | At all switchgear work positions |

4. TOOLS, EQUIPMENT & MATERIALS

| # | Tool / Equipment / Material | Specification / Standard | Qty Required | Inspected? |
| --- | --- | --- | --- | --- |
| 1 | Approved voltage detector (two units) | Rated for system voltage — calibrated | 2 | ☐ |
| 2 | Personal padlock — one per worker | Individual lock unique to each person | 1 per worker | ☐ |
| 3 | Hasp / lockout clamp | Multi-lock rated | As required | ☐ |
| 4 | Lockout box | For complex multi-lock isolations | As required | ☐ |
| 5 | Danger tags — 'DO NOT OPERATE' | Printed, weatherproof | Minimum 1 per isolation point | ☐ |
| 6 | Electrically insulated tools — LV rated | IEC 60900 rated | Full kit | ☐ |
| 7 | Discharge rod / earthing rod | Rated for system voltage | For MV systems | ☐ |
| 8 | Written switching schedule / isolation record | Signed by Section 16(2) or authorised person | 1 | ☐ |

5. STEP-BY-STEP SAFE WORK PROCEDURE

STEP 1.  IDENTIFY ALL ENERGY SOURCES

- Identify ALL energy sources associated with the equipment to be worked on:

- → Electrical (MV, LV, UPS, battery-backed systems, VSD capacitors, SCADA signal circuits)

- → Mechanical (gravity-loaded equipment, springs, counterweights)

- → Pneumatic (compressed air actuators, instrument air systems)

- → Hydraulic (hydraulic actuators)

- → Stored energy (capacitor banks, charged cables, pressure vessels)

- Confirm isolation points for EACH energy source on the drawing. Do NOT proceed if isolation points are not identified.

STEP 2.  NOTIFY ALL AFFECTED PARTIES

- Notify the control room operator / shift supervisor that the equipment is to be isolated.

- Notify all other work groups who may be affected by or who work near the isolation.

- Obtain written authority to isolate from the authorised person (PTW issuer).

- Confirm the switching schedule has been reviewed and signed by a second authorised person.

STEP 3.  DE-ENERGISE — SHUT DOWN EQUIPMENT

- Bring equipment to a safe, controlled stop in normal operating sequence — do NOT emergency stop unless necessary.

- Operate the local isolator or control device to shut down the equipment.

- Confirm equipment has stopped — observe, listen, and feel for continued movement (mechanical, airflow, vibration).

STEP 4.  ISOLATE — OPEN ALL ISOLATION POINTS

- Open the main isolation point — upstream incomer breaker, isolator, or disconnector.

- Where multiple isolation points exist — open ALL of them. Never rely on one isolation point alone.

- For MV systems — follow the written switching schedule step-by-step. Tick each step as completed.

- Disconnect all UPS, battery-backed, or alternative supply feeds.

STEP 5.  APPLY LOCK & DANGER TAG

- EACH WORKER who will work on the isolated equipment applies THEIR OWN personal padlock to the isolation point, using the hasp.

- EVERY padlock must be unique to the person who applied it. Only that person may remove their lock.

- Apply a 'DANGER — DO NOT OPERATE' tag to every isolation point, signed and dated by the person applying.

- Where multiple isolation points exist — lock and tag EVERY ONE.

- For complex isolations with many isolation points — use a lockout box. Keys to all isolation point locks are placed inside. Each worker locks the lockout box with their own padlock.

STEP 6.  RELEASE STORED ENERGY

- Operate the control device in all directions to confirm pressure or stored energy has been released.

- For capacitors / VSDs: wait the full discharge time specified by the manufacturer (minimum 5 minutes for most VSDs). Then verify discharge with meter.

- For MV cables: apply discharge / earthing rods per applicable procedure after confirming dead.

- For spring-loaded mechanisms: mechanically pin or block in position.

STEP 7.  TEST FOR DEAD — MANDATORY SEQUENCE

- TEST THE TESTER: Use the approved voltage indicator to test on a KNOWN LIVE source to confirm the tester is working correctly.

- TEST THE CIRCUIT: Apply the approved voltage indicator to each conductor / phase of the equipment to be worked on. Test Phase-Phase AND Phase-Earth.

- TEST THE TESTER AGAIN: Re-test on the known live source to confirm the tester is still working.

- Only proceed if zero voltage is confirmed on ALL conductors AND both tester checks are positive.

- If any doubt — STOP. Repeat isolation procedure. Never work on equipment that has not been confirmed dead by this sequence.

STEP 8.  WORK MAY NOW PROCEED

- With all locks applied, all tags in place, stored energy released, and zero voltage confirmed — work may commence.

- Workers must stay within the scope of the PTW. Do NOT work outside the isolated zone without a new PTW.

- If any worker leaves the site — their padlock remains on. They must reapply and re-verify on return.

- The PTW issuer must be notified if any condition changes.

STEP 9.  RESTORATION — REMOVING ISOLATION (RE-ENERGISATION)

- Confirm ALL work is complete and signed off. All tools removed. All workers briefed and clear of the equipment.

- EACH WORKER removes ONLY THEIR OWN padlock. No person may remove another person's padlock — ever.

- The last padlock to be removed is the PTW issuer's lock. PTW is signed closed at this point.

- Remove all danger tags. Confirm all isolation points are being restored in the correct sequence (reverse of opening sequence).

- Close the PTW in writing. Notify control room / shift supervisor that equipment is being restored.

- Energise in the correct sequence per switching schedule. Confirm equipment runs normally.

6. INSPECTION HOLD POINTS & WITNESS POINTS

- Hold Point — PTW must be signed before any LOTO is applied

- Hold Point — 'Test for Dead' sequence must be verified by a second person for MV systems

- Hold Point — all locks removed and PTW closed before re-energisation

7. EMERGENCY RESPONSE

EMERGENCY PROCEDURE — SPECIFIC TO THIS ACTIVITY:

If a worker is found working on equipment that has NOT been properly isolated — STOP ALL WORK immediately. Notify EC&I Site Manager and Section 16(2). Conduct immediate incident investigation. Do not restart work until full re-isolation is completed.

GENERAL: Site emergency number — [Insert]. National emergency: 10177. EC&I Site Manager: [Cell]. Section 16(2) [Name]: [Cell].

Muster point: [Insert location]. In any emergency — evacuate first, account for all persons, then report.

8. WORKER ACKNOWLEDGEMENT

I confirm that this Method Statement has been explained to me in a language I understand, that I understand the identified hazards and the controls to be applied, and that I will work in accordance with this procedure at all times.

| # | Full Name | ID Number | Trade / Role | Signature | Date |
| --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |
| 2 |  |  |  |  |  |
| 3 |  |  |  |  |  |
| 4 |  |  |  |  |  |
| 5 |  |  |  |  |  |
| 6 |  |  |  |  |  |
| 7 |  |  |  |  |  |
| 8 |  |  |  |  |  |
| 9 |  |  |  |  |  |
| 10 |  |  |  |  |  |
| 11 |  |  |  |  |  |
| 12 |  |  |  |  |  |

| Method Statement Author | Construction Supervisor | EC&I Site Manager | Section 16(2) Approved |
| --- | --- | --- | --- |
| [Name] | [Name] | [Name] | [Name] |
| Signature: _______________________ | Signature: _______________________ | Signature: _______________________ | Signature: _______________________ |
| Date: ___________________________ | Date: ___________________________ | Date: ___________________________ | Date: ___________________________ |

MS-004 — 33kV OHL — Stringing, Hardware & Terminations MSE-HSE-MS-001-04

| MS Reference | MS-004 |
| --- | --- |
| Related RA | RA-005 (MSE-HSE-RA-001 — Risk Assessment Register) |
| Document Number | MSE-HSE-MS-001-04 |
| Project | [Project Name] |
| Prepared By | [Name] — [Role] |
| Approved By | [Name] — Manager, Projects |
| Date Prepared | [DD/MM/YYYY] |
| Review Date | [DD/MM/YYYY or after any scope change or incident] |
| Supervisor in Charge | [Name] |
| Gang / Discipline | [EC&I / OHL / Instrument / etc.] |

1. SCOPE & PURPOSE

This Method Statement covers the installation of 33kV Overhead Line conductors including conductor stringing, insulator and hardware installation, conductor terminations at towers/poles, and the procedure for working in proximity to the existing energised system. This is a HIGH RISK activity. Only qualified OHL personnel may execute this work.

2. PRE-CONDITIONS — DO NOT START WITHOUT CONFIRMING ALL ITEMS BELOW

⚠  STOP: Every item in this section must be confirmed BEFORE work commences. If ANY item cannot be confirmed — work does NOT start. Notify EC&I Site Manager.

- ☐  OHL erection team fully qualified — wireman's licences and OHL certificates verified and on file

- ☐  Minimum approach distance confirmed and documented — 33kV: 1.0m minimum (greater where practicable)

- ☐  All conductors to be worked on are earthed both sides of the working section — earth application record signed

- ☐  Mechanical clearance from line owner obtained in writing

- ☐  Stringing equipment inspected — conductor blocks, tensioner, engine, brakes all tested

- ☐  Toolbox talk completed with all OHL team — this method statement briefed in full

- ☐  PTW issued by authorised person

3. PERSONAL PROTECTIVE EQUIPMENT (PPE)

| PPE Item | Standard / Specification | Mandatory? |
| --- | --- | --- |
| Safety helmet with chin strap | SANS 1397 | MANDATORY — chin strap fastened when climbing |
| Safety boots with ankle support | SANS 20345 | MANDATORY |
| High-visibility vest | EN 471 Class 2 | MANDATORY |
| Full body harness — OHL type with work positioning loop | SANS 1354 / EN 361 | MANDATORY |
| Double lanyard with shock absorber | EN 355 | MANDATORY — 100% tie-off |
| OHL arc-rated gloves (rubber insulating + leather protector) | IEC 60903 Class 2 minimum | MANDATORY on tower |
| Arc flash rated clothing | ATPV ≥ 8 cal/cm² | MANDATORY for conductor termination work |
| Safety glasses | SANS 1425 | MANDATORY |
| Leather work gloves | EN 388 | MANDATORY — ground crew |

4. TOOLS, EQUIPMENT & MATERIALS

| # | Tool / Equipment / Material | Specification / Standard | Qty Required | Inspected? |
| --- | --- | --- | --- | --- |
| 1 | Conductor drum (correct conductor per stringing schedule) | Per line design | Per schedule | ☐ |
| 2 | Conductor stringing blocks — rated for conductor type | Manufacturer rated | Per structure | ☐ |
| 3 | Hydraulic tensioner / braking device | Rated for conductor pull | 1 | ☐ |
| 4 | Pulling machine (puller / engine) | Rated for conductor | 1 | ☐ |
| 5 | Pulling rope / pilot rope | Rated — HMPE or similar | Per span length | ☐ |
| 6 | Compression fittings / ferrules | Match conductor type and size | Per schedule | ☐ |
| 7 | Compression tool — hydraulic | Calibrated, dies match conductor | 1 | ☐ |
| 8 | Earthing sticks / short-circuit sets | Rated for 33kV — tested | Min 2 per working section | ☐ |
| 9 | Approved voltage detector (33kV rated) | Calibrated | 2 | ☐ |
| 10 | Sagging equipment — tension meter or theodolite | Calibrated | 1 | ☐ |
| 11 | Climbing equipment — lanyards, connectors, positioning lanyards | SANS 1354 rated, inspected | Per climber | ☐ |

5. STEP-BY-STEP SAFE WORK PROCEDURE

STEP 1.  SAFETY CLEARANCES — BEFORE ANYTHING ELSE

- Confirm written mechanical clearance received from the line owner / EPCM.

- Confirm earthing record: all conductors in the working section are earthed at both ends — verify earth application log is signed.

- Physically verify earths are applied using approved 33kV voltage detector: TEST TESTER → TEST CONDUCTOR → TEST TESTER again.

- Do NOT proceed until zero voltage is confirmed and earthing is physically verified.

- Confirm minimum approach distance is communicated to all workers — any energised conductor or equipment at 33kV: 1.0m absolute minimum.

- Confirm PTW is signed and in hand. Brief entire OHL team on PTW scope.

STEP 2.  SITE ESTABLISHMENT & EQUIPMENT SETUP

- Position tensioner at pull start point — firm, level ground. Anchor tensioner per manufacturer spec.

- Position puller at pull end — firm, level ground. Anchor puller.

- Install conductor stringing blocks on all structures between tensioner and puller. Correct block type for conductor — anti-rotation where required.

- Brief structure crews on communication protocol — radio communication at all times.

- Establish exclusion zone: no person on the ground below or within 5m laterally of the conductor path during stringing.

STEP 3.  PILOT ROPE INSTALLATION

- Install pilot rope through all stringing blocks from puller to tensioner position.

- Check pilot rope rating — minimum 2× expected pulling tension.

- Helicopter or manual installation of pilot rope — per OHL team standard practice for this route.

STEP 4.  CONDUCTOR STRINGING

- Connect conductor to pilot rope using correct pulling sock / grip — never pull on the conductor strand alone.

- Begin stringing at slow controlled speed — supervisor monitors conductor at each structure.

- Communication: dedicated radio contact between puller operator, tensioner operator, and all structure crews.

- Any signal STOP is final — all operations cease immediately until cleared by supervisor.

- Monitor conductor for twisting, snapping, or block jump — stop immediately if observed.

- Conductor must not contact ground at any point during stringing — adjust equipment if necessary.

STEP 5.  SAGGING & TENSIONING

- Sag conductor to design tension/sag per stringing sag chart for the ambient temperature on the day.

- Measure sag using theodolite or tension method as specified in the stringing schedule.

- Record measured sag for each span. Do not proceed to clamping until sag is within specification.

- Confirm with engineer if any span is outside tolerance.

STEP 6.  CONDUCTOR HARDWARE — CLAMPING

- Install vibration dampers, suspension/tension clamps, and spacers per hardware schedule.

- Torque all bolted hardware to manufacturer specification — use calibrated torque wrench. Record.

- For compression fittings — use hydraulic press with correct dies. Die marks must be continuous. Record die number and press used.

STEP 7.  CONDUCTOR TERMINATION AT TOWER / POLE

- Ensure earth is still applied both sides of working section. Re-verify before any person ascends.

- Climber applies harness, checks all PPE, attaches first lanyard to anchor BEFORE leaving ground.

- 100% tie-off at all times — attach second lanyard before releasing first. Never unattached.

- Install compression dead-end fitting using hydraulic compression tool. Correct dies for conductor. Ensure full compression — check die gap indicator.

- Clean all insulator surfaces with clean dry cloth. No contamination on insulator surfaces.

- Connect conductor to insulator string hardware and structure anchor per drawing — torque to specification.

STEP 8.  REMOVAL OF EARTHS — CONTROLLED SEQUENCE

- Only remove earths once ALL conductor installation and hardware work is fully complete.

- Remove earths in reverse of application order — far end first.

- Record removal of each earth on the earthing record log.

- Confirm to PTW issuer that all earths have been removed and all workers are clear.

- PTW may only be closed after this confirmation.

6. INSPECTION HOLD POINTS & WITNESS POINTS

- Hold Point — earth application record signed before any person ascends

- Hold Point — 33kV voltage verification (test for dead) on each working section

- Witness Point — conductor sagging check (engineer or site manager)

- QC Hold Point — compression fitting inspection — die marks continuous and full length

7. EMERGENCY RESPONSE

EMERGENCY PROCEDURE — SPECIFIC TO THIS ACTIVITY:

Conductor contact / electrocution: Do NOT touch the person until the line is confirmed dead and earthed. Shout for help. Call site emergency number and 10177. Notify EC&I Site Manager and Section 16(2) immediately. Preserve scene. Do not restore supply until DoEL inspector authorises.

GENERAL: Site emergency number — [Insert]. National emergency: 10177. EC&I Site Manager: [Cell]. Section 16(2) [Name]: [Cell].

Muster point: [Insert location]. In any emergency — evacuate first, account for all persons, then report.

8. WORKER ACKNOWLEDGEMENT

I confirm that this Method Statement has been explained to me in a language I understand, that I understand the identified hazards and the controls to be applied, and that I will work in accordance with this procedure at all times.

| # | Full Name | ID Number | Trade / Role | Signature | Date |
| --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |
| 2 |  |  |  |  |  |
| 3 |  |  |  |  |  |
| 4 |  |  |  |  |  |
| 5 |  |  |  |  |  |
| 6 |  |  |  |  |  |
| 7 |  |  |  |  |  |
| 8 |  |  |  |  |  |
| 9 |  |  |  |  |  |
| 10 |  |  |  |  |  |
| 11 |  |  |  |  |  |
| 12 |  |  |  |  |  |

| Method Statement Author | Construction Supervisor | EC&I Site Manager | Section 16(2) Approved |
| --- | --- | --- | --- |
| [Name] | [Name] | [Name] | [Name] |
| Signature: _______________________ | Signature: _______________________ | Signature: _______________________ | Signature: _______________________ |
| Date: ___________________________ | Date: ___________________________ | Date: ___________________________ | Date: ___________________________ |

MS-005 — Earthing Mat & Grid Installation MSE-HSE-MS-001-05

| MS Reference | MS-005 |
| --- | --- |
| Related RA | RA-008 (MSE-HSE-RA-001 — Risk Assessment Register) |
| Document Number | MSE-HSE-MS-001-05 |
| Project | [Project Name] |
| Prepared By | [Name] — [Role] |
| Approved By | [Name] — Manager, Projects |
| Date Prepared | [DD/MM/YYYY] |
| Review Date | [DD/MM/YYYY or after any scope change or incident] |
| Supervisor in Charge | [Name] |
| Gang / Discipline | [EC&I / OHL / Instrument / etc.] |

1. SCOPE & PURPOSE

This Method Statement covers the excavation, installation, testing, and backfilling of earthing mat, earth grid, and earth conductor systems — including copper tape, copper conductor, earth rods, and thermite/exothermic welded connections.

2. PRE-CONDITIONS — DO NOT START WITHOUT CONFIRMING ALL ITEMS BELOW

⚠  STOP: Every item in this section must be confirmed BEFORE work commences. If ANY item cannot be confirmed — work does NOT start. Notify EC&I Site Manager.

- ☐  AFC earthing drawing available and reviewed

- ☐  Services drawing reviewed and CAT scan completed prior to any excavation

- ☐  Excavation inspection regime established — competent person appointed for daily excavation inspection

- ☐  Thermite welding team trained — thermite welding certificate on file

- ☐  Earth resistance test equipment calibrated and available

- ☐  PTW issued for any excavation within 500mm of identified services

- ☐  Toolbox talk completed — this method statement briefed in full

3. PERSONAL PROTECTIVE EQUIPMENT (PPE)

| PPE Item | Standard / Specification | Mandatory? |
| --- | --- | --- |
| Safety helmet | SANS 1397 | MANDATORY |
| Safety boots — steel toe, ankle height | SANS 20345 | MANDATORY |
| High-visibility vest | EN 471 Class 2 | MANDATORY |
| Safety glasses | SANS 1425 | MANDATORY |
| Work gloves — leather | EN 388 | MANDATORY |
| Face shield (for thermite welding) | ANSI Z87.1 | MANDATORY during welding |
| Leather welding gloves | EN 388 + EN 407 | MANDATORY during thermite welding |
| Fire-resistant clothing | EN ISO 11612 | MANDATORY during thermite welding |
| Gumboots / wellington boots | SABS rated | In wet or muddy trench conditions |

4. TOOLS, EQUIPMENT & MATERIALS

| # | Tool / Equipment / Material | Specification / Standard | Qty Required | Inspected? |
| --- | --- | --- | --- | --- |
| 1 | Copper earth tape / conductor (size per drawing) | Per BS 6360 / SANS 10142 | As per BOM | ☐ |
| 2 | Earth rods (copper-bonded steel, 16mm dia) | SANS 62561 / BS 7430 | Per drawing | ☐ |
| 3 | Earth rod driver — pneumatic or manual | Match rod OD | 1 | ☐ |
| 4 | Thermite weld kit (crucible, mould, powder) | Correct mould for conductor size | Per schedule | ☐ |
| 5 | Earth clamps — mechanical (backup connections) | Rated — tinned copper preferred | Per schedule | ☐ |
| 6 | CAT scanner (cable avoidance tool) | Calibrated | 1 | ☐ |
| 7 | Excavator — mini plant | Trained operator + banksman | As required | ☐ |
| 8 | Shoring / excavation supports | Rated for depth / soil type | Per plan | ☐ |
| 9 | Earth resistance test equipment — fall of potential or clamp | Calibrated | 1 | ☐ |
| 10 | Steel tape measure / builder's line | Calibrated | 1 | ☐ |

5. STEP-BY-STEP SAFE WORK PROCEDURE

STEP 1.  SERVICES VERIFICATION BEFORE EXCAVATION

- Review all underground services drawings for the proposed excavation area.

- Complete CAT scan using cable avoidance tool (CAT) on a 1m grid over the full excavation area.

- Mark all detected services with spray paint / marker flags on the surface.

- Within 500mm of any detected service — HAND DIG ONLY. No mechanical excavation.

- If any unmarked service is encountered during excavation — STOP immediately. Notify EC&I Site Manager.

STEP 2.  EXCAVATION — TRENCHES & PITS

- Excavate trenches to depth specified on drawing — minimum 600mm below finished grade unless otherwise specified.

- Excavated material to be placed minimum 500mm from trench edge to prevent surcharge collapse.

- For depths >1m: install shoring or batch/bench the trench before anyone enters. Comply with CR Reg 11.

- Competent person to inspect excavation every morning before any entry. Sign the excavation inspection register.

- Place barriers and signage around all open excavations. Cover open excavations when not actively working.

STEP 3.  EARTH ROD INSTALLATION

- Position earth rod at location per drawing. Vertical drive unless drawing shows angled installation.

- Drive rod using approved rod driver — do NOT use hammer directly on rod. Protect rod top with driving cap.

- Drive to full depth per drawing — typically 1.2m or 1.5m. If rod refuses — investigate soil condition, do not force.

- Leave minimum 200mm exposed for connection to earth conductor.

- Inspect rod head after driving — confirm no deformation or cracks in coating.

STEP 4.  EARTH CONDUCTOR LAYING

- Lay earth conductor (copper tape or round conductor) in trench bottom — clean, debris-free.

- Conductor to be flat in trench — no coiling, no sharp bends, no kinking.

- At all changes in direction — use minimum bend radius of 5× conductor width.

- Tape conductor to trench bottom using sand or fine aggregate bedding layer — 50mm bedding below, 100mm surround.

- Cross all other services with minimum 50mm clearance — use separator where clearance cannot be maintained.

STEP 5.  THERMITE (EXOTHERMIC) WELDING — CONNECTIONS

- Select correct mould for conductor size and type of connection. Refer to manufacturer matrix.

- Clean both conductors at the connection point — wire brush to bright copper.

- Clamp mould firmly over conductors — secure per manufacturer instruction.

- Pour correct charge of thermite powder into crucible. Insert ignition disc. Close and lock mould.

- Clear all non-essential personnel from 3m radius. Operator wears face shield, leather gloves, FR clothing.

- Ignite: single action — stand clear immediately.

- Allow to cool for minimum 60 seconds. Do NOT touch or move until cool.

- Open mould. Remove slag with brush. Inspect weld — must be full cross-section, no voids, no porosity.

- Failed welds must be cut out and re-welded. Never repair a thermite weld — cut out and start again.

STEP 6.  EARTH RESISTANCE TESTING

- Test resistance of completed earth grid using fall-of-potential method or calibrated clamp meter.

- Target: earth grid resistance ≤ 1Ω per SANS 10142 (or as specified on drawing).

- Record all test results — test point, resistance, test method, equipment serial number, date.

- If resistance is >1Ω — install additional earth rods per engineer's direction. Re-test after each addition.

- QC Officer to witness final test. Client to co-sign earth resistance test results.

STEP 7.  BACKFILLING

- Compact first 100mm of backfill by hand — do not use mechanical compaction within 100mm of conductor.

- Lay marker tape ('CAUTION — BURIED EARTH CONDUCTOR') 150mm below finished surface.

- Continue backfill in 150mm layers — compact each layer before proceeding.

- Mechanical compaction may be used above 300mm from conductor — no heavy compaction equipment until 600mm cover.

- Record backfill levels and compaction method in site diary.

- Update as-built drawing to show actual earth conductor routing and rod positions.

6. INSPECTION HOLD POINTS & WITNESS POINTS

- Hold Point — CAT scan result and services clearance before excavation

- Hold Point — excavation depth and shoring inspection (daily) before entry

- Hold Point — thermite weld inspection — each weld before backfilling

- QC Hold Point — earth resistance test ≤1Ω witnessed by QC Officer and Client

7. EMERGENCY RESPONSE

EMERGENCY PROCEDURE — SPECIFIC TO THIS ACTIVITY:

Worker trapped in excavation collapse: Do NOT enter the excavation — this could cause further collapse. Call site emergency number and 10177 immediately. If safe to do so — reach or throw a rope to the trapped person. Notify EC&I Site Manager and Section 16(2). Preserve scene.

GENERAL: Site emergency number — [Insert]. National emergency: 10177. EC&I Site Manager: [Cell]. Section 16(2) [Name]: [Cell].

Muster point: [Insert location]. In any emergency — evacuate first, account for all persons, then report.

8. WORKER ACKNOWLEDGEMENT

I confirm that this Method Statement has been explained to me in a language I understand, that I understand the identified hazards and the controls to be applied, and that I will work in accordance with this procedure at all times.

| # | Full Name | ID Number | Trade / Role | Signature | Date |
| --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |
| 2 |  |  |  |  |  |
| 3 |  |  |  |  |  |
| 4 |  |  |  |  |  |
| 5 |  |  |  |  |  |
| 6 |  |  |  |  |  |
| 7 |  |  |  |  |  |
| 8 |  |  |  |  |  |
| 9 |  |  |  |  |  |
| 10 |  |  |  |  |  |
| 11 |  |  |  |  |  |
| 12 |  |  |  |  |  |

| Method Statement Author | Construction Supervisor | EC&I Site Manager | Section 16(2) Approved |
| --- | --- | --- | --- |
| [Name] | [Name] | [Name] | [Name] |
| Signature: _______________________ | Signature: _______________________ | Signature: _______________________ | Signature: _______________________ |
| Date: ___________________________ | Date: ___________________________ | Date: ___________________________ | Date: ___________________________ |

MS-006 — Pre-Commissioning, Loop Testing & System Energisation MSE-HSE-MS-001-06

| MS Reference | MS-006 |
| --- | --- |
| Related RA | RA-010 (MSE-HSE-RA-001 — Risk Assessment Register) |
| Document Number | MSE-HSE-MS-001-06 |
| Project | [Project Name] |
| Prepared By | [Name] — [Role] |
| Approved By | [Name] — Manager, Projects |
| Date Prepared | [DD/MM/YYYY] |
| Review Date | [DD/MM/YYYY or after any scope change or incident] |
| Supervisor in Charge | [Name] |
| Gang / Discipline | [EC&I / OHL / Instrument / etc.] |

1. SCOPE & PURPOSE

This Method Statement covers the pre-commissioning sequence for EC&I systems — including IR testing, loop verification (4–20mA), motor run checks, and the formal first energisation procedure for LV and MV systems. This is a HIGH RISK activity requiring Section 16(2) sign-off before energisation.

2. PRE-CONDITIONS — DO NOT START WITHOUT CONFIRMING ALL ITEMS BELOW

⚠  STOP: Every item in this section must be confirmed BEFORE work commences. If ANY item cannot be confirmed — work does NOT start. Notify EC&I Site Manager.

- ☐  All installation inspections complete — ITP Hold Points signed off

- ☐  Quality Dossier pre-commissioning section complete — all IR tests recorded, loop check sheet prepared

- ☐  Pre-commissioning punch list compiled and all Cat A items closed

- ☐  Arc flash study reviewed — correct cal/cm² PPE identified for each system

- ☐  Written energisation procedure prepared and signed by EC&I Site Manager and Section 16(2)

- ☐  Client / EPCM representative available and has signed the pre-energisation checklist

- ☐  PTW system in place — all PTWs for pre-commissioning phase issued and controlled

- ☐  All non-essential personnel clear of the commissioning zone

3. PERSONAL PROTECTIVE EQUIPMENT (PPE)

| PPE Item | Standard / Specification | Mandatory? |
| --- | --- | --- |
| Safety helmet | SANS 1397 | MANDATORY |
| Safety boots | SANS 20345 | MANDATORY |
| Safety glasses | SANS 1425 | MANDATORY |
| LV arc flash PPE — 4 cal/cm² minimum | NFPA 70E / IEC 61482 | MANDATORY for LV energisation |
| MV arc flash PPE — 12 cal/cm² minimum | NFPA 70E / IEC 61482 | MANDATORY for MV energisation |
| Arc flash face shield — rated to applicable cal/cm² | NFPA 70E | MANDATORY for all energisation |
| Electrically insulated gloves — Class 00 (LV) or Class 2 (MV) | IEC 60903 | MANDATORY during energisation |
| Arc flash rated clothing (FR) | ATPV rated | MANDATORY for MV work |
| Rubber insulating mat | IEC 61111 | At all switchgear positions |

4. TOOLS, EQUIPMENT & MATERIALS

| # | Tool / Equipment / Material | Specification / Standard | Qty Required | Inspected? |
| --- | --- | --- | --- | --- |
| 1 | IR test equipment — 500VDC (LV), 5kVDC (MV) | Calibrated — certificate on site | 1 | ☐ |
| 2 | Loop calibrator / HART communicator | Calibrated | 1 | ☐ |
| 3 | Digital multimeter — CAT III/IV | Calibrated | 2 | ☐ |
| 4 | Phase sequence meter | Calibrated | 1 | ☐ |
| 5 | Clamp meter — AC/DC | Calibrated | 1 | ☐ |
| 6 | Thermal imaging camera | Calibrated — for post-energisation thermal scan | 1 | ☐ |
| 7 | Approved voltage detector — LV and MV rated | Calibrated — 2 units | 2 | ☐ |
| 8 | Pre-commissioning checklist and loop check sheets | Current revision | Full set | ☐ |
| 9 | Quality Dossier (for recording all test results) | Current revision | 1 | ☐ |
| 10 | Radio communication equipment | Charged and tested | Per team member | ☐ |

5. STEP-BY-STEP SAFE WORK PROCEDURE

STEP 1.  INSULATION RESISTANCE (IR) TESTING — ALL CABLES & EQUIPMENT

- Confirm all cables are terminated at BOTH ends before IR testing.

- Disconnect all sensitive equipment (PLCs, transmitters, VSD control boards) from circuits being tested.

- Set IR tester to correct voltage: 500VDC for LV control / instrument cables, 500VDC–1kVDC for LV power, 5kVDC for MV cables.

- Warning posted at both ends of cable being tested — 'HIGH VOLTAGE TESTING IN PROGRESS — DO NOT TOUCH'.

- Two-person test: one operates tester, one guards remote end.

- Apply test voltage for minimum 60 seconds. Record reading after 60 seconds.

- Acceptance: LV power cables ≥ 1MΩ at 500VDC. Control/instrument ≥ 100MΩ at 500VDC. MV ≥ 100MΩ at 5kVDC.

- After test: DISCHARGE cable to earth for minimum 4× test time. Verify discharged with meter before touching.

- Record all results on IR Test Register (MSE-IR2-001).

STEP 2.  LOOP TESTING — 4–20mA SIGNAL VERIFICATION

- Before loop testing: inhibit all associated control outputs in the DCS/PLC — confirm inhibit with control room operator.

- Confirm all field devices for the loop are installed and connected.

- Inject 4mA at field device (or loop calibrator): confirm 0% reading at DCS/HMI. Accept ±0.1mA.

- Inject 12mA: confirm 50% reading at DCS/HMI. Accept ±0.1mA.

- Inject 20mA: confirm 100% reading at DCS/HMI. Accept ±0.1mA.

- Verify alarm setpoints trigger at correct values. Record on Loop Check Register (MSE-LOOP-001).

- Verify HART communication if HART devices installed — read device tag ID from HART communicator.

- QC Officer and Client co-sign each completed loop.

STEP 3.  MOTOR RUN CHECKS — PRE-COUPLING

- Confirm motor is mechanically de-coupled from driven equipment.

- Confirm motor alignment has been verified by mechanical team.

- Check phase sequence with phase sequence meter at motor terminals — confirm rotation direction against motor nameplate.

- Apply power momentarily — jog the motor. Observe: correct rotation direction, no unusual noise, no vibration.

- If rotation is incorrect — stop immediately. Swap any 2 phases at motor terminal box. Re-check rotation. Never swap at MCC.

- Run motor for 30 seconds uncoupled. Monitor: temperature, vibration, current draw vs nameplate.

- Record motor run data on pre-commissioning checklist. Mechanical team to couple after sign-off.

STEP 4.  PRE-ENERGISATION CHECKLIST — FINAL VERIFICATION

- EC&I Site Manager to complete and sign the pre-energisation checklist — every item initialled.

- Section 16(2) ([Name]) to review and countersign the pre-energisation checklist.

- Client / EPCM H&S and engineering representative to countersign — energisation authority granted.

- Confirm all PTWs for work on this system are CLOSED.

- Confirm all LOTO locks have been removed from the system being energised.

- Confirm all test equipment, tools, and personnel are clear of the equipment.

- Arc flash PPE confirmed — all personnel at the switchgear wearing correct cal/cm² PPE.

STEP 5.  FIRST ENERGISATION — LV SYSTEM

- Non-essential personnel clear of the switchroom. Maximum 2 authorised persons in the room during energisation.

- Stand to the side of the panel — never directly in front of the busbars or door during energisation.

- Close the incomer breaker following the written switching sequence — one step at a time.

- Monitor: no tripping, no unusual noise, no smell of burning. 5 second pause between steps.

- If any abnormality — trip the incomer immediately. Investigate before proceeding.

- After successful energisation — thermal imaging scan of all connections within 30 minutes of loading.

STEP 6.  FIRST ENERGISATION — MV SYSTEM

- MV energisation: minimum 10m exclusion zone for all non-essential personnel.

- Arc flash PPE mandatory — minimum 12 cal/cm² for 33kV switching.

- Remote racking of VCB where available — never manually rack a VCB in with body in front of the panel.

- Switching sequence to be read out loud step-by-step and independently verified by second person.

- Each step confirmed complete before next step proceeds.

- Client / EPCM commissioning engineer must be present for all MV energisation.

- Record all switching operations — breaker position, time, operator, witness.

STEP 7.  POST-ENERGISATION CHECKS

- Thermal imaging scan of all connections within 30 minutes of applying load.

- Record thermal scan results — flag any connection >5°C above ambient as a defect requiring investigation.

- Check all protection relay setpoints against protection study settings list.

- Record all measured voltages, currents, and power factor readings on commissioning sheet.

- Complete commissioning sign-off — EC&I Site Manager, Client / EPCM, QC Officer.

- File all pre-commissioning and commissioning records in Quality Dossier under correct system boundary.

6. INSPECTION HOLD POINTS & WITNESS POINTS

- Hold Point — IR test results accepted and signed off by QC Officer before energisation

- Hold Point — pre-energisation checklist signed by EC&I Site Manager AND Section 16(2)

- Hold Point — Client / EPCM countersign required before MV energisation

- Witness Point — first energisation — client representative must be present

7. EMERGENCY RESPONSE

EMERGENCY PROCEDURE — SPECIFIC TO THIS ACTIVITY:

Arc flash or electrical fire: Activate fire alarm. Evacuate immediately. Do NOT fight electrical fires with water. Use CO₂ extinguisher only. Call site emergency number and fire station. Notify EC&I Site Manager and Section 16(2) immediately. No re-entry until line authority confirms safe.

GENERAL: Site emergency number — [Insert]. National emergency: 10177. EC&I Site Manager: [Cell]. Section 16(2) [Name]: [Cell].

Muster point: [Insert location]. In any emergency — evacuate first, account for all persons, then report.

8. WORKER ACKNOWLEDGEMENT

I confirm that this Method Statement has been explained to me in a language I understand, that I understand the identified hazards and the controls to be applied, and that I will work in accordance with this procedure at all times.

| # | Full Name | ID Number | Trade / Role | Signature | Date |
| --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |
| 2 |  |  |  |  |  |
| 3 |  |  |  |  |  |
| 4 |  |  |  |  |  |
| 5 |  |  |  |  |  |
| 6 |  |  |  |  |  |
| 7 |  |  |  |  |  |
| 8 |  |  |  |  |  |
| 9 |  |  |  |  |  |
| 10 |  |  |  |  |  |
| 11 |  |  |  |  |  |
| 12 |  |  |  |  |  |

| Method Statement Author | Construction Supervisor | EC&I Site Manager | Section 16(2) Approved |
| --- | --- | --- | --- |
| [Name] | [Name] | [Name] | [Name] |
| Signature: _______________________ | Signature: _______________________ | Signature: _______________________ | Signature: _______________________ |
| Date: ___________________________ | Date: ___________________________ | Date: ___________________________ | Date: ___________________________ |