| MEEKAS STAR ENGINEERING | EC&I RISK ASSESSMENT REGISTER |
| --- | --- |
| PROJECTS DEPARTMENT · EC&I CONSTRUCTION · RISK ASSESSMENT REGISTER | MSE-HSE-RA-001 · Rev 01 · 2025 |

EC&I CONSTRUCTION

RISK ASSESSMENT REGISTER

OHS ACT 85/1993  ·  CONSTRUCTION REGULATIONS 2014  ·  SANS 10142  ·  IEC 60364  ·  IEC 60079

| Document Number | MSE-HSE-RA-001 · Rev 01 · 2025 |
| --- | --- |
| Principal Contractor | Meekas Star Engineering Service Limited — Projects Department |
| Project Name | [Insert Project Name] |
| Project Number | [Insert Project Number] |
| Client / EPCM | [Insert Client Name] |
| Site Location | [Insert Site Location] |
| Scope | EC&I Construction — MV to LV, OHL, Switchgear, MCC, Instruments, Small Power, Lighting, Earthing |
| Prepared By | [Name] — [Role] |
| Approved By | [Name] — Manager, Projects |
| Client Acceptance | [Name] — [Role] — [Date] |
| Review Frequency | Monthly or after any incident or scope change |
| Legal Basis | OHS Act 85/1993 · Construction Regulations 2014 · General Safety Regulations |

RISK RATING MATRIX  —  Risk Score = Likelihood × Severity

| RATING | 1–3 LOW | 4–7 LOW-MED | 8–14 MEDIUM | 15–19 HIGH | 20–25 CRITICAL |
| --- | --- | --- | --- | --- | --- |
| LIKELIHOOD (L) | 1 — Rare Almost never happens | 2 — Unlikely Could happen but rarely | 3 — Possible May happen occasionally | 4 — Likely Will probably happen | 5 — Almost Certain Expected to happen |
| SEVERITY (S) | 1 — Negligible No injury or minimal FA | 2 — Minor First aid required | 3 — Moderate MTI — lost days | 4 — Major LTI — serious injury | 5 — Catastrophic Fatality / permanent disability |

| Prepared By | Reviewed By | Approved By | Client Approval |
| --- | --- | --- | --- |
| [Name] — [Role] | [EC&I Site Manager] | [Name] — Manager Projects | [Name] — [Company] |
| Signature: _______________________ | Signature: _______________________ | Signature: _______________________ | Signature: _______________________ |
| Date: ___________________________ | Date: ___________________________ | Date: ___________________________ | Date: ___________________________ |

| MEEKAS STAR ENGINEERING | TABLE OF CONTENTS |
| --- | --- |
| PROJECTS DEPARTMENT · EC&I CONSTRUCTION · RISK ASSESSMENT REGISTER | MSE-HSE-RA-001 |

| RA Ref | Doc Ref | Risk Assessment Title | Page |
| --- | --- | --- | --- |
| RA-001 | MSE-HSE-RA-001-01 | Cable Ladder & Tray Installation | — |
| RA-002 | MSE-HSE-RA-001-02 | Cable Pulling Operations | — |
| RA-003 | MSE-HSE-RA-001-03 | Cable Terminations — LV & MV | — |
| RA-004 | MSE-HSE-RA-001-04 | MV & LV Switchgear Installation | — |
| RA-005 | MSE-HSE-RA-001-05 | 33kV Overhead Line (OHL) — Stringing & Termination | — |
| RA-006 | MSE-HSE-RA-001-06 | Motor Control Centre (MCC) Installation & Commissioning | — |
| RA-007 | MSE-HSE-RA-001-07 | Instrument & Field Device Installation | — |
| RA-008 | MSE-HSE-RA-001-08 | Earthing, Bonding & Earthing Mat / Grid Installation | — |
| RA-009 | MSE-HSE-RA-001-09 | Small Power & Lighting Installation | — |
| RA-010 | MSE-HSE-RA-001-10 | Pre-Commissioning, Loop Testing & Energisation | — |

RA-001 — CABLE LADDER & TRAY INSTALLATION MSE-HSE-RA-001-01

| RA Reference | RA-001 | Document Number | MSE-HSE-RA-001-01 |
| --- | --- | --- | --- |
| Activity Title | Cable Ladder & Tray Installation | Revision | Rev 01 · 2025 |
| Prepared By | [Name] — [Role] | Approved By | [Name] — Manager, Projects |
| Project | [Project Name] | Site Location | [Site Location] |
| Date Prepared | [DD/MM/YYYY] | Review Date | [DD/MM/YYYY or after incident] |
| Supervisor in Charge | [Name] | Client H&S Accepted By | [Name] — [Date] |

ACTIVITY DESCRIPTION:

All activities associated with the installation of cable ladder, cable tray, and associated supports — including setting out, support installation, and ladder/tray fixing at ground level and at height.

HIERARCHY OF CONTROLS APPLIED:  1. Elimination  →  2. Substitution  →  3. Engineering Controls  →  4. Administrative Controls  →  5. PPE

| Task Step / Activity | Identified Hazard | Who is at Risk | Potential Injury / Incident | L | S | Initial Risk Rating | Controls & Preventive Measures to be Applied | R-L | R-S | Residual Risk Rating | Responsible Person |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Setting out & marking | Falls on same level — uneven terrain, obstructions | All workers | Trips, sprains, fractures | 3 | 2 | 6 LOW | Clear work area before starting, wear safety boots, maintain housekeeping | 1 | 2 | 2 NEGLIGIBLE | Site Supervisor |
| Setting out & marking | Manual handling — heavy sections | Workers handling material | Musculoskeletal injury, back strain | 3 | 3 | 9 MEDIUM | Max 25kg per person, team lifts, mechanical aids for >50kg | 2 | 2 | 4 LOW | Site Supervisor |
| Drilling / anchoring into concrete or steelwork | Dust inhalation from concrete drilling | Workers nearby | Respiratory irritation, silicosis | 3 | 3 | 9 MEDIUM | P2 dust masks, wet drilling where possible, isolate work area | 2 | 2 | 4 LOW | Supervisor |
| Drilling / anchoring into concrete or steelwork | Eye injury from drill bits, sparks, and fragments | Drillers & nearby workers | Eye damage, possible blindness | 4 | 4 | 16 HIGH | Safety glasses mandatory, face shield for overhead drilling, exclusion zone | 2 | 3 | 6 LOW | Supervisor |
| Drilling / anchoring into concrete or steelwork | Striking concealed services (electrical, piping) | Worker drilling | Electrocution, gas release, flooding | 3 | 5 | 15 HIGH | Services drawing review, cable avoidance scan (CAT) before drilling, hand probe | 2 | 4 | 8 MEDIUM | EC&I Site Manager |
| Working at height — elevated ladder installation | Falls from height >2m | All elevated workers | Serious injury, fatality | 4 | 5 | 20 CRITICAL | Full body harness + double lanyard, tested anchor points (15kN), never work alone at height, exclusion zone below | 2 | 4 | 8 MEDIUM | Construction Supervisor |
| Working at height — elevated ladder installation | Falling objects — tools, fixings, ladder sections | Workers below | Head injury, fatality | 4 | 4 | 16 HIGH | Hard hats mandatory, tool tethering, toe boards on platforms, exclusion zone signed | 2 | 3 | 6 LOW | Construction Supervisor |
| Working at height — elevated ladder installation | Structural instability — scaffold or MEWP failure | Elevated workers | Collapse, fall, fatality | 2 | 5 | 10 MEDIUM | Scaffold inspected and tagged green, MEWP with valid certificate, weight limits observed | 1 | 5 | 5 LOW | Competent Inspector |
| Cutting ladder sections | Cuts and lacerations — angle grinder, hacksaw | Worker cutting | Lacerations, amputations | 4 | 3 | 12 MEDIUM | Cut-resistant gloves, face shield, secure workpiece, correct disc type, no loose clothing | 2 | 2 | 4 LOW | Supervisor |
| Cutting ladder sections | Fire / sparks from grinding near cables | All in area | Fire, cable damage | 3 | 4 | 12 MEDIUM | Hot work permit, fire extinguisher standby, remove combustibles >3m, fire watch 30min post | 2 | 2 | 4 LOW | Supervisor |
| Cable ladder earthing & bonding | Electric shock from inadvertent contact with live circuit | Electrician / fitter | Electrical shock, cardiac arrest | 3 | 5 | 15 HIGH | Verify dead before bonding, LOTO applied, test before touch, insulated tools | 2 | 4 | 8 MEDIUM | EC&I Site Manager |
| Final inspection | Contact with sharp edges on cut ladder | Inspector | Lacerations | 3 | 2 | 6 LOW | Cut-resistant gloves, file or de-burr all cut ends, awareness | 1 | 2 | 2 NEGLIGIBLE | QC Officer |

WORKER ACKNOWLEDGEMENT — I confirm that I have been briefed on this risk assessment, understand the identified hazards and the controls that must be applied, and agree to work in accordance with these controls:

| # | Full Name | ID Number | Trade / Role | Signature | Date |
| --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |
| 2 |  |  |  |  |  |
| 3 |  |  |  |  |  |
| 4 |  |  |  |  |  |
| 5 |  |  |  |  |  |
| 6 |  |  |  |  |  |
| 7 |  |  |  |  |  |
| 8 |  |  |  |  |  |
| 9 |  |  |  |  |  |
| 10 |  |  |  |  |  |

| Risk Assessment Author | Construction Supervisor | EC&I Site Manager | Section 16(2) — Approved |
| --- | --- | --- | --- |
| [Name] | [Name] | [Name] | [Name] |
| Signature: _______________________ | Signature: _______________________ | Signature: _______________________ | Signature: _______________________ |
| Date: ___________________________ | Date: ___________________________ | Date: ___________________________ | Date: ___________________________ |

RA-002 — CABLE PULLING OPERATIONS MSE-HSE-RA-001-02

| RA Reference | RA-002 | Document Number | MSE-HSE-RA-001-02 |
| --- | --- | --- | --- |
| Activity Title | Cable Pulling Operations | Revision | Rev 01 · 2025 |
| Prepared By | [Name] — [Role] | Approved By | [Name] — Manager, Projects |
| Project | [Project Name] | Site Location | [Site Location] |
| Date Prepared | [DD/MM/YYYY] | Review Date | [DD/MM/YYYY or after incident] |
| Supervisor in Charge | [Name] | Client H&S Accepted By | [Name] — [Date] |

ACTIVITY DESCRIPTION:

All activities associated with cable installation including cable drum handling, cable routing, mechanical and manual cable pulling through conduit, ducts, cable tray, and cable ladder.

HIERARCHY OF CONTROLS APPLIED:  1. Elimination  →  2. Substitution  →  3. Engineering Controls  →  4. Administrative Controls  →  5. PPE

| Task Step / Activity | Identified Hazard | Who is at Risk | Potential Injury / Incident | L | S | Initial Risk Rating | Controls & Preventive Measures to be Applied | R-L | R-S | Residual Risk Rating | Responsible Person |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Cable drum offloading & positioning | Crush injury — cable drum roll-away or overturning | All in area | Crush injury, fatality | 4 | 5 | 20 CRITICAL | Chock drums on both sides immediately on positioning, never stand in drum path, crane/forklift with rated SWL | 2 | 4 | 8 MEDIUM | Site Supervisor |
| Cable drum offloading & positioning | Overturning of drum spindle stand | Workers | Drum drop, crush injury | 3 | 4 | 12 MEDIUM | Rated spindle stands, inspect before use, level ground, load within SWL | 2 | 3 | 6 LOW | Supervisor |
| Mechanical cable pulling | Entanglement in cable pulling winch or capstan | Operators | Entanglement, degloving, amputation | 3 | 5 | 15 HIGH | Guards on all rotating parts, loose clothing prohibited, designated operator only, e-stop tested | 1 | 4 | 4 LOW | EC&I Site Manager |
| Mechanical cable pulling | Cable snap-back / conductor whip | All in area | Eye injury, lacerations, blunt trauma | 3 | 4 | 12 MEDIUM | Clear of pull axis, face shield worn, rated pulling eyes and grips, rated swivels, max tension monitoring | 2 | 3 | 6 LOW | Supervisor |
| Manual cable pulling | Musculoskeletal injury — repetitive pulling, awkward posture | Pulling gang | Back strain, hernia, repetitive strain | 4 | 3 | 12 MEDIUM | Team pulls, rotate workers every 15min, mechanical assist where possible, trained technique | 2 | 2 | 4 LOW | Supervisor |
| Pulling through conduit | Hand / finger trap — conduit entry or midspan guides | Workers guiding cable | Crush, lacerations | 3 | 3 | 9 MEDIUM | Bell-mouth conduit entries, gloves, clear communication signals between puller and feeder | 2 | 2 | 4 LOW | Supervisor |
| Working near energised circuits | Electric shock during cable routing near live equipment | Electricians | Shock, electrocution | 3 | 5 | 15 HIGH | Confirm isolation of adjacent circuits, PTW active, test before touching any conductor | 2 | 4 | 8 MEDIUM | EC&I Site Manager |
| Cable identification & tagging | Confusion of cable IDs leading to incorrect connection | All | Electrical fault, equipment damage, shock | 3 | 4 | 12 MEDIUM | Cable tagged at both ends immediately after pulling, checked against drum schedule before moving | 2 | 2 | 4 LOW | QC Officer |
| Outdoor cable pulling — heat exposure | Heat stress / heat stroke | All outdoor workers | Heat exhaustion, collapse | 3 | 3 | 9 MEDIUM | Regular breaks, shaded rest area, min 500ml water/hr, buddy system, heat illness briefing | 2 | 2 | 4 LOW | Supervisor |

WORKER ACKNOWLEDGEMENT — I confirm that I have been briefed on this risk assessment, understand the identified hazards and the controls that must be applied, and agree to work in accordance with these controls:

| # | Full Name | ID Number | Trade / Role | Signature | Date |
| --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |
| 2 |  |  |  |  |  |
| 3 |  |  |  |  |  |
| 4 |  |  |  |  |  |
| 5 |  |  |  |  |  |
| 6 |  |  |  |  |  |
| 7 |  |  |  |  |  |
| 8 |  |  |  |  |  |
| 9 |  |  |  |  |  |
| 10 |  |  |  |  |  |

| Risk Assessment Author | Construction Supervisor | EC&I Site Manager | Section 16(2) — Approved |
| --- | --- | --- | --- |
| [Name] | [Name] | [Name] | [Name] |
| Signature: _______________________ | Signature: _______________________ | Signature: _______________________ | Signature: _______________________ |
| Date: ___________________________ | Date: ___________________________ | Date: ___________________________ | Date: ___________________________ |

RA-003 — CABLE TERMINATIONS — LV & MV MSE-HSE-RA-001-03

| RA Reference | RA-003 | Document Number | MSE-HSE-RA-001-03 |
| --- | --- | --- | --- |
| Activity Title | Cable Terminations — LV & MV | Revision | Rev 01 · 2025 |
| Prepared By | [Name] — [Role] | Approved By | [Name] — Manager, Projects |
| Project | [Project Name] | Site Location | [Site Location] |
| Date Prepared | [DD/MM/YYYY] | Review Date | [DD/MM/YYYY or after incident] |
| Supervisor in Charge | [Name] | Client H&S Accepted By | [Name] — [Date] |

ACTIVITY DESCRIPTION:

All activities associated with the termination of LV and MV cables including cable preparation, glanding, ferrule crimping, termination to terminals, and MV jointing/termination kits.

HIERARCHY OF CONTROLS APPLIED:  1. Elimination  →  2. Substitution  →  3. Engineering Controls  →  4. Administrative Controls  →  5. PPE

| Task Step / Activity | Identified Hazard | Who is at Risk | Potential Injury / Incident | L | S | Initial Risk Rating | Controls & Preventive Measures to be Applied | R-L | R-S | Residual Risk Rating | Responsible Person |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Cable preparation — stripping, cutting | Cuts and lacerations from cable knife, strippers, snips | Terminator | Lacerations | 4 | 3 | 12 MEDIUM | Cut-resistant gloves, cut away from body, retractable blade knives, secure cable | 2 | 2 | 4 LOW | Supervisor |
| Verifying cable is dead | Shock from residual charge or incorrect isolation | Terminator | Electric shock, electrocution | 4 | 5 | 20 CRITICAL | Test for dead using approved voltage detector. Test the tester — test circuit — test tester again. Do not rely on drawings alone | 2 | 5 | 10 MEDIUM | EC&I Site Manager |
| LV terminations at switchboard / MCC | Arc flash from inadvertent energisation | Electrician | Arc flash burns, blindness, fatality | 3 | 5 | 15 HIGH | Arc flash PPE (min 4 cal/cm²) for LV panels, PTW, LOTO confirmed, co-worker briefed | 2 | 4 | 8 MEDIUM | EC&I Site Manager |
| MV terminations — stress cone installation | Arc flash / HV shock during MV jointing | MV terminator | Electrocution, arc flash, fatality | 3 | 5 | 15 HIGH | Qualified MV jointer only, arc flash suit (min 12 cal/cm² for MV), gloves rated for voltage, minimum approach distance | 1 | 5 | 5 LOW | EC&I Site Manager |
| MV terminations — stress cone installation | Chemical exposure from jointing compounds / resin | Jointer | Skin and eye irritation, sensitisation | 3 | 3 | 9 MEDIUM | Chemical-resistant gloves, safety glasses, SDS on site, ventilation, no eating near chemicals | 2 | 2 | 4 LOW | Supervisor |
| Ferrule crimping — mechanical or hydraulic tool | Hand crush injury from hydraulic crimp tool | Terminator | Crush injury | 3 | 3 | 9 MEDIUM | Correct die size, inspect tool before use, no hands near jaw during operation, two-hand grip | 2 | 2 | 4 LOW | Supervisor |
| Glanding — MV & LV cable glands | Flying debris from rotating reamer or armour cutting | Terminator | Eye injury | 4 | 3 | 12 MEDIUM | Safety glasses, face shield for overhead glanding, controlled cutting | 2 | 2 | 4 LOW | Supervisor |
| Testing post-termination — IR test | Electric shock from HV test voltage (500–5000VDC) | Tester & bystanders | Shock, cardiac arrest | 3 | 5 | 15 HIGH | Warning posted, area cleared before HV applied, rated test leads, HV insulated gloves, one person on tester, another on warning | 2 | 4 | 8 MEDIUM | EC&I Site Manager |
| Testing post-termination — IR test | Inadvertent discharge of charged capacitance post-test | Tester | Shock | 3 | 4 | 12 MEDIUM | Discharge cable to earth after each test, verified with meter before touching, earth left on between tests | 2 | 3 | 6 LOW | EC&I Site Manager |
| Working in confined panel space | Heat stress from working inside energised panel room | Worker | Heat exhaustion, fainting | 3 | 3 | 9 MEDIUM | Air conditioning or forced ventilation in panel rooms, break schedule, buddy system | 2 | 2 | 4 LOW | Supervisor |

WORKER ACKNOWLEDGEMENT — I confirm that I have been briefed on this risk assessment, understand the identified hazards and the controls that must be applied, and agree to work in accordance with these controls:

| # | Full Name | ID Number | Trade / Role | Signature | Date |
| --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |
| 2 |  |  |  |  |  |
| 3 |  |  |  |  |  |
| 4 |  |  |  |  |  |
| 5 |  |  |  |  |  |
| 6 |  |  |  |  |  |
| 7 |  |  |  |  |  |
| 8 |  |  |  |  |  |
| 9 |  |  |  |  |  |
| 10 |  |  |  |  |  |

| Risk Assessment Author | Construction Supervisor | EC&I Site Manager | Section 16(2) — Approved |
| --- | --- | --- | --- |
| [Name] | [Name] | [Name] | [Name] |
| Signature: _______________________ | Signature: _______________________ | Signature: _______________________ | Signature: _______________________ |
| Date: ___________________________ | Date: ___________________________ | Date: ___________________________ | Date: ___________________________ |

RA-004 — MV & LV SWITCHGEAR INSTALLATION MSE-HSE-RA-001-04

| RA Reference | RA-004 | Document Number | MSE-HSE-RA-001-04 |
| --- | --- | --- | --- |
| Activity Title | MV & LV Switchgear Installation | Revision | Rev 01 · 2025 |
| Prepared By | [Name] — [Role] | Approved By | [Name] — Manager, Projects |
| Project | [Project Name] | Site Location | [Site Location] |
| Date Prepared | [DD/MM/YYYY] | Review Date | [DD/MM/YYYY or after incident] |
| Supervisor in Charge | [Name] | Client H&S Accepted By | [Name] — [Date] |

ACTIVITY DESCRIPTION:

All activities associated with the installation, alignment, internal wiring verification, and pre-energisation testing of MV and LV switchboards, ring main units (RMUs), and associated switchgear equipment.

HIERARCHY OF CONTROLS APPLIED:  1. Elimination  →  2. Substitution  →  3. Engineering Controls  →  4. Administrative Controls  →  5. PPE

| Task Step / Activity | Identified Hazard | Who is at Risk | Potential Injury / Incident | L | S | Initial Risk Rating | Controls & Preventive Measures to be Applied | R-L | R-S | Residual Risk Rating | Responsible Person |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Unloading and positioning switchgear | Crane or forklift use — panel drop, overturn | All in area | Crush, fatality | 3 | 5 | 15 HIGH | Lifting plan, rated lifting lugs, SWL observed, banksman, exclusion zone during lift, level surface | 2 | 4 | 8 MEDIUM | Site Supervisor |
| Unloading and positioning switchgear | Mechanical handling on skates/rollers — runaway | Workers | Crush injury | 3 | 4 | 12 MEDIUM | Chock at each move, controlled slope gradient, spotters on both sides, tag lines | 2 | 3 | 6 LOW | Supervisor |
| Physical installation — bolting down | Struck by — shifting panel on uneven floor | Workers stabilising | Crush, trapped fingers | 3 | 3 | 9 MEDIUM | Panel braced until permanently fixed, hand positions clear before lowering, co-workers clear | 2 | 2 | 4 LOW | Supervisor |
| Internal wiring & connection verification | Contact with residual stored energy (capacitors, VT secondaries) | Electrician | Shock, burns | 3 | 4 | 12 MEDIUM | Discharge capacitors before contact, block VT secondaries, LOTO on all energy sources | 2 | 3 | 6 LOW | EC&I Site Manager |
| Energisation of MV switchgear | Arc flash during first energisation | Electrician / commissioning engineer | Arc flash, burns, fatality | 3 | 5 | 15 HIGH | Arc flash study completed, correct PPE (cal/cm²), remote racking where possible, all non-essential clear, commissioning procedure followed | 1 | 5 | 5 LOW | EC&I Site Manager |
| Energisation of MV switchgear | SF₆ gas leak (where applicable) | All in area | Asphyxiation, environmental | 2 | 4 | 8 MEDIUM | Gas detection equipment, trained operators, gas recovery system, ventilation, no naked flames | 1 | 4 | 4 LOW | EC&I Site Manager |
| Operation of VCB / ACB breakers | Incorrect operation sequence leading to fault | Operator | Arc flash, equipment damage | 3 | 5 | 15 HIGH | Written switching schedule, independent verification, one person per breaker, communication protocol | 2 | 4 | 8 MEDIUM | EC&I Site Manager |
| Working in energised switchroom | Inadvertent contact with live busbars | All in switchroom | Electrocution, arc flash | 2 | 5 | 10 MEDIUM | Full arc flash PPE in energised rooms, minimum approach distance maintained, no tools left on live parts | 1 | 5 | 5 LOW | EC&I Site Manager |
| Temporary power connections for commissioning | Incorrect polarity / phase sequence | Electrician | Equipment damage, short circuit | 3 | 3 | 9 MEDIUM | Phase sequence test before connection, colour coding verified, continuity check | 2 | 2 | 4 LOW | EC&I Site Manager |

WORKER ACKNOWLEDGEMENT — I confirm that I have been briefed on this risk assessment, understand the identified hazards and the controls that must be applied, and agree to work in accordance with these controls:

| # | Full Name | ID Number | Trade / Role | Signature | Date |
| --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |
| 2 |  |  |  |  |  |
| 3 |  |  |  |  |  |
| 4 |  |  |  |  |  |
| 5 |  |  |  |  |  |
| 6 |  |  |  |  |  |
| 7 |  |  |  |  |  |
| 8 |  |  |  |  |  |
| 9 |  |  |  |  |  |
| 10 |  |  |  |  |  |

| Risk Assessment Author | Construction Supervisor | EC&I Site Manager | Section 16(2) — Approved |
| --- | --- | --- | --- |
| [Name] | [Name] | [Name] | [Name] |
| Signature: _______________________ | Signature: _______________________ | Signature: _______________________ | Signature: _______________________ |
| Date: ___________________________ | Date: ___________________________ | Date: ___________________________ | Date: ___________________________ |

RA-005 — 33KV OVERHEAD LINE (OHL) — STRINGING & TERMINATION MSE-HSE-RA-001-05

| RA Reference | RA-005 | Document Number | MSE-HSE-RA-001-05 |
| --- | --- | --- | --- |
| Activity Title | 33kV Overhead Line (OHL) — Stringing & Termination | Revision | Rev 01 · 2025 |
| Prepared By | [Name] — [Role] | Approved By | [Name] — Manager, Projects |
| Project | [Project Name] | Site Location | [Site Location] |
| Date Prepared | [DD/MM/YYYY] | Review Date | [DD/MM/YYYY or after incident] |
| Supervisor in Charge | [Name] | Client H&S Accepted By | [Name] — [Date] |

ACTIVITY DESCRIPTION:

All activities associated with the erection of 33kV OHL structures, conductor stringing, insulator installation, and conductor terminations. This is a HIGH RISK activity — qualified OHL team only.

HIERARCHY OF CONTROLS APPLIED:  1. Elimination  →  2. Substitution  →  3. Engineering Controls  →  4. Administrative Controls  →  5. PPE

| Task Step / Activity | Identified Hazard | Who is at Risk | Potential Injury / Incident | L | S | Initial Risk Rating | Controls & Preventive Measures to be Applied | R-L | R-S | Residual Risk Rating | Responsible Person |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Structure erection — concrete/steel poles | Structural collapse during erection | All in area | Crush, fatality | 3 | 5 | 15 HIGH | Engineered erection procedure, crane rated for load, exclusion zone 1.5× pole height, trained riggers | 2 | 5 | 10 MEDIUM | Construction Supervisor |
| Structure erection — concrete/steel poles | Falls from structure during climbing | Climbers | Serious injury, fatality | 4 | 5 | 20 CRITICAL | Full body harness, double lanyard, certified climbing equipment, dedicated safety officer present | 2 | 5 | 10 MEDIUM | Construction Supervisor |
| Conductor stringing | Contact with existing energised conductors / lines | All on site | Electrocution, fatality | 3 | 5 | 15 HIGH | Minimum approach distance enforced, crossing structures earthed, safe crossing procedures, spotter at all times | 1 | 5 | 5 LOW | EC&I Site Manager |
| Conductor stringing | Conductor snap-back / whip — drum runaway or brake failure | All in stringing zone | Serious injury, fatality | 3 | 5 | 15 HIGH | Rated braking systems, inspected before use, no persons in conductor path, tag lines, communication protocol per tower | 1 | 5 | 5 LOW | EC&I Site Manager |
| Conductor stringing | Falling hardware — insulators, conductor, clamps | Ground workers | Head injury, fatality | 4 | 4 | 16 HIGH | Hard hats mandatory, exclusion zone under stringing, never stand below workers at height | 2 | 3 | 6 LOW | Supervisor |
| Insulator and hardware installation | Falls from height — at tower crossarm level | Climbers | Serious injury, fatality | 4 | 5 | 20 CRITICAL | Full body harness, 100% tie-off, work at one attachment point at a time, no simultaneous climbers on same structure | 2 | 4 | 8 MEDIUM | Construction Supervisor |
| Conductor termination at towers | Electrical contact — conductor not isolated / earthed | Terminator | Electrocution, fatality | 3 | 5 | 15 HIGH | Earth all conductors before touching — both sides of the working section, verify with approved detector | 1 | 5 | 5 LOW | EC&I Site Manager |
| Ground-level activities — vehicle interaction | Struck by construction vehicles | Ground workers | Serious injury, fatality | 3 | 4 | 12 MEDIUM | Traffic management plan, flagmen, 20km/h speed limit, hi-vis mandatory, pedestrian exclusion from vehicle lanes | 2 | 3 | 6 LOW | Supervisor |
| Energisation | Incorrect phase sequence or missing earth removed | All near line | Fault, electrocution | 2 | 5 | 10 MEDIUM | Written energisation checklist, independent check, Docc of all earths, all persons clear before energisation command | 1 | 5 | 5 LOW | EC&I Site Manager |

WORKER ACKNOWLEDGEMENT — I confirm that I have been briefed on this risk assessment, understand the identified hazards and the controls that must be applied, and agree to work in accordance with these controls:

| # | Full Name | ID Number | Trade / Role | Signature | Date |
| --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |
| 2 |  |  |  |  |  |
| 3 |  |  |  |  |  |
| 4 |  |  |  |  |  |
| 5 |  |  |  |  |  |
| 6 |  |  |  |  |  |
| 7 |  |  |  |  |  |
| 8 |  |  |  |  |  |
| 9 |  |  |  |  |  |
| 10 |  |  |  |  |  |

| Risk Assessment Author | Construction Supervisor | EC&I Site Manager | Section 16(2) — Approved |
| --- | --- | --- | --- |
| [Name] | [Name] | [Name] | [Name] |
| Signature: _______________________ | Signature: _______________________ | Signature: _______________________ | Signature: _______________________ |
| Date: ___________________________ | Date: ___________________________ | Date: ___________________________ | Date: ___________________________ |

RA-006 — MOTOR CONTROL CENTRE (MCC) INSTALLATION & COMMISSIONING MSE-HSE-RA-001-06

| RA Reference | RA-006 | Document Number | MSE-HSE-RA-001-06 |
| --- | --- | --- | --- |
| Activity Title | Motor Control Centre (MCC) Installation & Commissioning | Revision | Rev 01 · 2025 |
| Prepared By | [Name] — [Role] | Approved By | [Name] — Manager, Projects |
| Project | [Project Name] | Site Location | [Site Location] |
| Date Prepared | [DD/MM/YYYY] | Review Date | [DD/MM/YYYY or after incident] |
| Supervisor in Charge | [Name] | Client H&S Accepted By | [Name] — [Date] |

ACTIVITY DESCRIPTION:

All activities associated with the physical installation, internal wiring verification, and commissioning of Motor Control Centres including star-delta starters, VSD drives, and direct-on-line starters.

HIERARCHY OF CONTROLS APPLIED:  1. Elimination  →  2. Substitution  →  3. Engineering Controls  →  4. Administrative Controls  →  5. PPE

| Task Step / Activity | Identified Hazard | Who is at Risk | Potential Injury / Incident | L | S | Initial Risk Rating | Controls & Preventive Measures to be Applied | R-L | R-S | Residual Risk Rating | Responsible Person |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| MCC offloading & positioning | Mechanical handling — crane, forklift | All in area | Crush, structural damage | 3 | 4 | 12 MEDIUM | Lifting plan, rated lifting points, banksman, level floor, exclusion zone during lift | 2 | 3 | 6 LOW | Supervisor |
| Mechanical fixing and levelling | Struck by — shifting MCC on uneven surface | Workers | Crush injury | 3 | 3 | 9 MEDIUM | Braced until permanently fixed, hand positions clear before levelling, wedges inspected | 2 | 2 | 4 LOW | Supervisor |
| Internal wiring verification | Contact with stored energy in capacitors (VSD) | Electrician | Shock, burns | 4 | 4 | 16 HIGH | Wait full discharge time (per VSD manufacturer — typically 5min+), verify with meter, LOTO maintained | 2 | 3 | 6 LOW | EC&I Site Manager |
| VSD parameter programming | Incorrect parameter causing uncontrolled motor start | Commissioning engineer | Equipment damage, personnel injury from unexpected movement | 3 | 4 | 12 MEDIUM | Mechanical brake applied during parameterisation, area around driven equipment cleared, emergency stop tested first | 2 | 3 | 6 LOW | EC&I Site Manager |
| Point-to-point wiring check | Incorrect wiring causing phase fault | Electrician | Short circuit, arc flash, fire | 3 | 4 | 12 MEDIUM | Systematic P2P from drawings, independent verification, correct ferrule labelling, torque to spec | 2 | 3 | 6 LOW | EC&I Site Manager |
| First motor run — star-delta or DOL | Unexpected motor rotation — wrong direction | All near motor | Mechanical damage, injury to maintenance personnel near coupling | 3 | 3 | 9 MEDIUM | Decouple motor before first run, verify rotation before coupling, exclusion zone at motor end | 2 | 2 | 4 LOW | EC&I Site Manager |
| First motor run — VSD | VSD fault — overcurrent, earth fault | Electrician / commissioning | Arc flash, equipment damage | 3 | 4 | 12 MEDIUM | Remote operation first run, arc flash PPE, fuses correct rating, protection settings verified | 2 | 3 | 6 LOW | EC&I Site Manager |
| Commissioning under load | Thermal overload leading to fire | All in area | Fire, equipment damage | 2 | 3 | 6 LOW | Overload settings verified before load test, thermal imaging on first load run, fire extinguisher standby | 1 | 3 | 3 NEGLIGIBLE | EC&I Site Manager |
| Working in energised MCC | Inadvertent contact with live busbars during commissioning | Electrician | Electrocution, arc flash | 3 | 5 | 15 HIGH | Full arc flash PPE in live MCC, minimum approach distance, tools insulated, no unsupervised live work | 2 | 4 | 8 MEDIUM | EC&I Site Manager |

WORKER ACKNOWLEDGEMENT — I confirm that I have been briefed on this risk assessment, understand the identified hazards and the controls that must be applied, and agree to work in accordance with these controls:

| # | Full Name | ID Number | Trade / Role | Signature | Date |
| --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |
| 2 |  |  |  |  |  |
| 3 |  |  |  |  |  |
| 4 |  |  |  |  |  |
| 5 |  |  |  |  |  |
| 6 |  |  |  |  |  |
| 7 |  |  |  |  |  |
| 8 |  |  |  |  |  |
| 9 |  |  |  |  |  |
| 10 |  |  |  |  |  |

| Risk Assessment Author | Construction Supervisor | EC&I Site Manager | Section 16(2) — Approved |
| --- | --- | --- | --- |
| [Name] | [Name] | [Name] | [Name] |
| Signature: _______________________ | Signature: _______________________ | Signature: _______________________ | Signature: _______________________ |
| Date: ___________________________ | Date: ___________________________ | Date: ___________________________ | Date: ___________________________ |

RA-007 — INSTRUMENT & FIELD DEVICE INSTALLATION MSE-HSE-RA-001-07

| RA Reference | RA-007 | Document Number | MSE-HSE-RA-001-07 |
| --- | --- | --- | --- |
| Activity Title | Instrument & Field Device Installation | Revision | Rev 01 · 2025 |
| Prepared By | [Name] — [Role] | Approved By | [Name] — Manager, Projects |
| Project | [Project Name] | Site Location | [Site Location] |
| Date Prepared | [DD/MM/YYYY] | Review Date | [DD/MM/YYYY or after incident] |
| Supervisor in Charge | [Name] | Client H&S Accepted By | [Name] — [Date] |

ACTIVITY DESCRIPTION:

All activities associated with the installation of field instrumentation including transmitters, control valves, solenoid valves, actuators, junction boxes, and associated impulse tubing and signal cabling.

HIERARCHY OF CONTROLS APPLIED:  1. Elimination  →  2. Substitution  →  3. Engineering Controls  →  4. Administrative Controls  →  5. PPE

| Task Step / Activity | Identified Hazard | Who is at Risk | Potential Injury / Incident | L | S | Initial Risk Rating | Controls & Preventive Measures to be Applied | R-L | R-S | Residual Risk Rating | Responsible Person |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Installation at height — on vessels, structures | Falls from height | Workers | Serious injury, fatality | 4 | 5 | 20 CRITICAL | Full body harness, double lanyard, work platform, MEWP where practical, exclusion zone below | 2 | 4 | 8 MEDIUM | Supervisor |
| Installation in process areas | Exposure to hazardous process fluids / gases | All in process area | Chemical burns, inhalation, poisoning | 3 | 4 | 12 MEDIUM | Identify process hazards before entry, ATEX rated tools in hazardous areas, SDS on file, buddy system | 2 | 3 | 6 LOW | Supervisor |
| Installation in ATEX / hazardous areas | Spark ignition from non-ATEX tools or equipment | All in zone | Fire, explosion, fatality | 3 | 5 | 15 HIGH | Only ATEX rated tools in classified zones, no mobile phones in Zone 0/1, verify zone classification before entry | 1 | 5 | 5 LOW | EC&I Site Manager |
| Impulse tubing installation | Burns from process fluid contact during impulse connection | Instrument tech | Chemical burns, scalds | 3 | 4 | 12 MEDIUM | Verify process isolation, bleed pressure before breaking containment, face shield, chemical gloves | 2 | 3 | 6 LOW | Supervisor |
| Junction box installation & wiring | Shock from signal cables incorrectly assumed dead | Instrument tech | Shock | 3 | 3 | 9 MEDIUM | Verify all field cables dead, LOTO, test before touch — instrument signals can still carry dangerous voltage in some configurations | 2 | 2 | 4 LOW | EC&I Site Manager |
| Control valve installation | Pinch / crush from actuator movement | Workers | Crushed fingers, hands | 3 | 4 | 12 MEDIUM | Isolate instrument air before work, vent actuator fully, do not place hands inside actuator housing | 2 | 3 | 6 LOW | Supervisor |
| Working in confined spaces (vessels) | Oxygen deficiency / toxic atmosphere | All in confined space | Asphyxiation, poisoning, fatality | 2 | 5 | 10 MEDIUM | Gas test before entry, continuous monitoring, rescue team on standby, no lone working in CS | 1 | 5 | 5 LOW | EC&I Site Manager |
| Hand tools — drilling, cutting | Cuts, eye injuries | Instrument tech | Lacerations, eye damage | 4 | 3 | 12 MEDIUM | Safety glasses, cut-resistant gloves, tool inspected before use | 2 | 2 | 4 LOW | Supervisor |

WORKER ACKNOWLEDGEMENT — I confirm that I have been briefed on this risk assessment, understand the identified hazards and the controls that must be applied, and agree to work in accordance with these controls:

| # | Full Name | ID Number | Trade / Role | Signature | Date |
| --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |
| 2 |  |  |  |  |  |
| 3 |  |  |  |  |  |
| 4 |  |  |  |  |  |
| 5 |  |  |  |  |  |
| 6 |  |  |  |  |  |
| 7 |  |  |  |  |  |
| 8 |  |  |  |  |  |
| 9 |  |  |  |  |  |
| 10 |  |  |  |  |  |

| Risk Assessment Author | Construction Supervisor | EC&I Site Manager | Section 16(2) — Approved |
| --- | --- | --- | --- |
| [Name] | [Name] | [Name] | [Name] |
| Signature: _______________________ | Signature: _______________________ | Signature: _______________________ | Signature: _______________________ |
| Date: ___________________________ | Date: ___________________________ | Date: ___________________________ | Date: ___________________________ |

RA-008 — EARTHING, BONDING & EARTHING MAT / GRID INSTALLATION MSE-HSE-RA-001-08

| RA Reference | RA-008 | Document Number | MSE-HSE-RA-001-08 |
| --- | --- | --- | --- |
| Activity Title | Earthing, Bonding & Earthing Mat / Grid Installation | Revision | Rev 01 · 2025 |
| Prepared By | [Name] — [Role] | Approved By | [Name] — Manager, Projects |
| Project | [Project Name] | Site Location | [Site Location] |
| Date Prepared | [DD/MM/YYYY] | Review Date | [DD/MM/YYYY or after incident] |
| Supervisor in Charge | [Name] | Client H&S Accepted By | [Name] — [Date] |

ACTIVITY DESCRIPTION:

All activities associated with the installation of earthing systems including earth pits, earth rods, copper tape/conductor, earthing mats, and earth grid network — including associated excavation work.

HIERARCHY OF CONTROLS APPLIED:  1. Elimination  →  2. Substitution  →  3. Engineering Controls  →  4. Administrative Controls  →  5. PPE

| Task Step / Activity | Identified Hazard | Who is at Risk | Potential Injury / Incident | L | S | Initial Risk Rating | Controls & Preventive Measures to be Applied | R-L | R-S | Residual Risk Rating | Responsible Person |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Excavation for earth grid — trenching | Excavation collapse / burial | Workers in/near excavation | Burial, suffocation, fatality | 3 | 5 | 15 HIGH | Shoring for depths >1m, no entry without daily inspection, battering or benching, exclusion zone | 2 | 4 | 8 MEDIUM | Construction Supervisor |
| Excavation for earth grid — trenching | Striking underground services | Worker excavating | Electrocution, gas explosion, flooding | 3 | 5 | 15 HIGH | Services drawings reviewed, CAT scan before excavation, hand dig within 500mm of services | 2 | 4 | 8 MEDIUM | EC&I Site Manager |
| Excavation for earth grid — trenching | Falls into open excavation | Workers near edge | Fractures, head injury | 4 | 3 | 12 MEDIUM | Barriers and signage around all open excavations, lighting if working after dark, covers when unattended | 2 | 2 | 4 LOW | Supervisor |
| Excavation for earth grid — trenching | Plant / vehicle overrun into excavation | All near excavation | Excavation collapse, fatality | 3 | 5 | 15 HIGH | Exclusion zone 1m from edge for plant, spotter/banksman, barriers, adequate lighting | 2 | 4 | 8 MEDIUM | Supervisor |
| Earth rod installation — driving | Flying debris from rod driver | Workers | Eye injury, lacerations | 3 | 3 | 9 MEDIUM | Safety glasses, face shield, correct driver for rod size, inspection of rod driver before use | 2 | 2 | 4 LOW | Supervisor |
| Earth conductor installation — copper tape | Manual handling — heavy copper rolls | Workers | Musculoskeletal strain | 3 | 2 | 6 LOW | Mechanical dispensers for heavy rolls, team handling, trolleys | 2 | 1 | 2 NEGLIGIBLE | Supervisor |
| Thermite / exothermic welding of connections | Burns from molten metal splash | Workers | Burns to skin and eyes | 4 | 4 | 16 HIGH | Face shield, leather gloves, fire-resistant clothing, dry conditions only, training required for thermite welding | 2 | 3 | 6 LOW | Supervisor |
| Thermite / exothermic welding of connections | Fire from thermite weld in dry vegetation or combustibles | All in area | Fire | 3 | 4 | 12 MEDIUM | Hot work permit, clear combustibles 3m, fire extinguisher standby, fire watch 30min post-weld | 2 | 3 | 6 LOW | Supervisor |
| Earth resistance testing — clamp or fall-of-potential | Electric shock from test equipment | Tester | Shock | 2 | 3 | 6 LOW | Insulated test leads, rated test equipment, verify adjacent circuits de-energised during HV injection tests | 1 | 2 | 2 NEGLIGIBLE | EC&I Site Manager |
| Backfilling earth trenches | Striking buried conductor with compaction equipment | Workers | Damage to earth grid, shock risk | 3 | 3 | 9 MEDIUM | Mark conductor depth on trench, hand compact first 300mm over conductor, inspect before mechanical compaction | 2 | 2 | 4 LOW | Supervisor |

WORKER ACKNOWLEDGEMENT — I confirm that I have been briefed on this risk assessment, understand the identified hazards and the controls that must be applied, and agree to work in accordance with these controls:

| # | Full Name | ID Number | Trade / Role | Signature | Date |
| --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |
| 2 |  |  |  |  |  |
| 3 |  |  |  |  |  |
| 4 |  |  |  |  |  |
| 5 |  |  |  |  |  |
| 6 |  |  |  |  |  |
| 7 |  |  |  |  |  |
| 8 |  |  |  |  |  |
| 9 |  |  |  |  |  |
| 10 |  |  |  |  |  |

| Risk Assessment Author | Construction Supervisor | EC&I Site Manager | Section 16(2) — Approved |
| --- | --- | --- | --- |
| [Name] | [Name] | [Name] | [Name] |
| Signature: _______________________ | Signature: _______________________ | Signature: _______________________ | Signature: _______________________ |
| Date: ___________________________ | Date: ___________________________ | Date: ___________________________ | Date: ___________________________ |

RA-009 — SMALL POWER & LIGHTING INSTALLATION MSE-HSE-RA-001-09

| RA Reference | RA-009 | Document Number | MSE-HSE-RA-001-09 |
| --- | --- | --- | --- |
| Activity Title | Small Power & Lighting Installation | Revision | Rev 01 · 2025 |
| Prepared By | [Name] — [Role] | Approved By | [Name] — Manager, Projects |
| Project | [Project Name] | Site Location | [Site Location] |
| Date Prepared | [DD/MM/YYYY] | Review Date | [DD/MM/YYYY or after incident] |
| Supervisor in Charge | [Name] | Client H&S Accepted By | [Name] — [Date] |

ACTIVITY DESCRIPTION:

All activities associated with the installation of small power distribution boards, socket outlets, surface wiring, conduit systems, lighting fixtures, emergency lighting, and final circuit connections.

HIERARCHY OF CONTROLS APPLIED:  1. Elimination  →  2. Substitution  →  3. Engineering Controls  →  4. Administrative Controls  →  5. PPE

| Task Step / Activity | Identified Hazard | Who is at Risk | Potential Injury / Incident | L | S | Initial Risk Rating | Controls & Preventive Measures to be Applied | R-L | R-S | Residual Risk Rating | Responsible Person |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Distribution board installation — fixing and mounting | Falls from ladders / steps | Worker on ladder | Fractures, head injury | 4 | 3 | 12 MEDIUM | Step ladder on firm level surface, 3-point contact, do not over-reach, spotter on ladder | 2 | 2 | 4 LOW | Supervisor |
| Distribution board installation — fixing and mounting | Heavy panel lift — musculoskeletal | Worker | Back strain | 3 | 3 | 9 MEDIUM | Two-person lift for panels >15kg, mechanical aids for heavier panels, lift below shoulder height | 2 | 2 | 4 LOW | Supervisor |
| Conduit installation — threading, bending | Cuts and eye injuries — conduit bender, die, swarf | Worker | Lacerations, eye injury | 4 | 3 | 12 MEDIUM | Safety glasses, cut-resistant gloves, inspect conduit dies before use, deburr all cut ends | 2 | 2 | 4 LOW | Supervisor |
| Wiring circuits and connections | Electric shock from live circuits | Electrician | Shock, electrocution | 3 | 5 | 15 HIGH | LOTO on all circuits, verify dead on all conductors, test before touch — upstream and downstream | 2 | 4 | 8 MEDIUM | EC&I Site Manager |
| Luminaire installation — overhead | Falls from height | Worker | Serious injury | 4 | 4 | 16 HIGH | Correct ladder or work platform for height, harness if >2m, spotter, tool bag for tools | 2 | 3 | 6 LOW | Supervisor |
| Luminaire installation — overhead | Falling luminaire during installation | Workers below | Head injury | 4 | 4 | 16 HIGH | Exclusion zone below, safety wire on all luminaires, locking mechanisms verified before releasing | 2 | 3 | 6 LOW | Supervisor |
| Emergency lighting — battery testing | Battery acid exposure | Electrician | Chemical burns to skin and eyes | 2 | 3 | 6 LOW | Insulated gloves, safety glasses, ventilation in battery room, no sparks near batteries, SDS available | 1 | 2 | 2 NEGLIGIBLE | Supervisor |
| Circuit testing — loop impedance / RCD test | Shock from test instruments on live circuits | Tester | Shock | 3 | 4 | 12 MEDIUM | Rated test instruments (CAT III/IV), insulated probes, one hand rule, safety glasses, check test lead integrity | 2 | 3 | 6 LOW | EC&I Site Manager |
| Working near other active trades | Struck by or contact with other trade activities | All workers | Various injuries | 3 | 3 | 9 MEDIUM | Toolbox talk daily, demarcation of work zones, communication between supervisors of all trades | 2 | 2 | 4 LOW | Supervisor |

WORKER ACKNOWLEDGEMENT — I confirm that I have been briefed on this risk assessment, understand the identified hazards and the controls that must be applied, and agree to work in accordance with these controls:

| # | Full Name | ID Number | Trade / Role | Signature | Date |
| --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |
| 2 |  |  |  |  |  |
| 3 |  |  |  |  |  |
| 4 |  |  |  |  |  |
| 5 |  |  |  |  |  |
| 6 |  |  |  |  |  |
| 7 |  |  |  |  |  |
| 8 |  |  |  |  |  |
| 9 |  |  |  |  |  |
| 10 |  |  |  |  |  |

| Risk Assessment Author | Construction Supervisor | EC&I Site Manager | Section 16(2) — Approved |
| --- | --- | --- | --- |
| [Name] | [Name] | [Name] | [Name] |
| Signature: _______________________ | Signature: _______________________ | Signature: _______________________ | Signature: _______________________ |
| Date: ___________________________ | Date: ___________________________ | Date: ___________________________ | Date: ___________________________ |

RA-010 — PRE-COMMISSIONING, LOOP TESTING & ENERGISATION MSE-HSE-RA-001-10

| RA Reference | RA-010 | Document Number | MSE-HSE-RA-001-10 |
| --- | --- | --- | --- |
| Activity Title | Pre-Commissioning, Loop Testing & Energisation | Revision | Rev 01 · 2025 |
| Prepared By | [Name] — [Role] | Approved By | [Name] — Manager, Projects |
| Project | [Project Name] | Site Location | [Site Location] |
| Date Prepared | [DD/MM/YYYY] | Review Date | [DD/MM/YYYY or after incident] |
| Supervisor in Charge | [Name] | Client H&S Accepted By | [Name] — [Date] |

ACTIVITY DESCRIPTION:

All activities associated with pre-commissioning checks, loop testing (4–20mA verification), HV proof testing, system energisation, and formal sign-off of electrical and instrumentation systems.

HIERARCHY OF CONTROLS APPLIED:  1. Elimination  →  2. Substitution  →  3. Engineering Controls  →  4. Administrative Controls  →  5. PPE

| Task Step / Activity | Identified Hazard | Who is at Risk | Potential Injury / Incident | L | S | Initial Risk Rating | Controls & Preventive Measures to be Applied | R-L | R-S | Residual Risk Rating | Responsible Person |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Loop testing — 4–20mA signal injection | Incorrect injection causing unexpected equipment movement (control valves, actuators) | All in field | Equipment damage, personnel injury | 3 | 4 | 12 MEDIUM | Inhibit associated control outputs before loop testing, field confirmed clear, communication with DCS operator | 2 | 3 | 6 LOW | EC&I Site Manager |
| Loop testing — 4–20mA signal injection | Contact with signal wiring assumed dead but with hazardous voltage | Instrument tech | Shock | 3 | 3 | 9 MEDIUM | Verify voltage level on all signal cables before touching, never assume safe | 2 | 2 | 4 LOW | EC&I Site Manager |
| HV insulation resistance testing — MV cables | Shock from 5kVDC test voltage applied to cables | Tester, bystanders | Electrocution, cardiac arrest | 3 | 5 | 15 HIGH | Warning posted, exclusion zone, rated HV test equipment, insulated gloves, two-person test — one at tester, one at remote end | 1 | 5 | 5 LOW | EC&I Site Manager |
| HV insulation resistance testing — MV cables | Residual capacitive charge remaining after test | Tester | Shock | 4 | 4 | 16 HIGH | Discharge to earth after every test, verify with meter, earth clips left on between moves | 2 | 3 | 6 LOW | EC&I Site Manager |
| First energisation — LV systems | Arc flash from first energisation | Electrician / commissioning | Burns, fatality | 3 | 5 | 15 HIGH | Arc flash PPE (NFPA 70E rated), remote racking where available, all non-essential personnel cleared, commissioning dossier signed | 2 | 4 | 8 MEDIUM | EC&I Site Manager |
| First energisation — MV systems | Arc flash, structural damage from MV fault | All in switchroom | Burns, fatality | 2 | 5 | 10 MEDIUM | Arc flash study reviewed, minimum cal/cm² PPE confirmed, energisation procedure signed off by client, all persons 10m clear minimum | 1 | 5 | 5 LOW | EC&I Site Manager |
| Instrument calibration with live process signals | Unexpected process condition during calibration | Instrument tech | Process upset, equipment damage, injury | 3 | 3 | 9 MEDIUM | Inhibit signals, inform control room before calibration, two-person team, communication throughout | 2 | 2 | 4 LOW | EC&I Site Manager |
| Motor runs under load | Unexpected mechanical failure — coupling, shaft, blade | All in motor area | Flying debris, injury | 3 | 4 | 12 MEDIUM | Exclusion zone at motor drive end, coupling guards in place before run, thermal monitoring during run | 2 | 3 | 6 LOW | EC&I Site Manager |
| Punch list closeout — final checks | Complacency during late-stage work — fatigue | All workers | All hazard types elevated | 3 | 3 | 9 MEDIUM | Toolbox talk to address late-stage complacency, no reduction in PPE or permit discipline at any stage | 2 | 2 | 4 LOW | Supervisor |

WORKER ACKNOWLEDGEMENT — I confirm that I have been briefed on this risk assessment, understand the identified hazards and the controls that must be applied, and agree to work in accordance with these controls:

| # | Full Name | ID Number | Trade / Role | Signature | Date |
| --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |
| 2 |  |  |  |  |  |
| 3 |  |  |  |  |  |
| 4 |  |  |  |  |  |
| 5 |  |  |  |  |  |
| 6 |  |  |  |  |  |
| 7 |  |  |  |  |  |
| 8 |  |  |  |  |  |
| 9 |  |  |  |  |  |
| 10 |  |  |  |  |  |

| Risk Assessment Author | Construction Supervisor | EC&I Site Manager | Section 16(2) — Approved |
| --- | --- | --- | --- |
| [Name] | [Name] | [Name] | [Name] |
| Signature: _______________________ | Signature: _______________________ | Signature: _______________________ | Signature: _______________________ |
| Date: ___________________________ | Date: ___________________________ | Date: ___________________________ | Date: ___________________________ |